| Princeton Plasma Physics Laboratory Procedure |
| --- |
| Procedure Title: Configuration and Access Control for the NSTX Central Instrumentation & Control System |
| Number C-NSTX-OP-AD-122 | Revision: 0 | Effective Date: ???______ Expiration Date: (2 yr. unless otherwise stipulated) |
| Procedure Approvals |  |
| Author P. Sichta | Date |
| ATI ???__________ | Date |
| RLM ???__________ | Date |
| Responsible Division: ???_______________ |  |
| Procedure Requirements designated by RLM Labwide: |  |
|  | Work Planning Form #_______(ENG-032) |  | Lockout/Tagout (ESH-016) |
|  | Confined Space Permit (5008, Sec. 8, Chap 5) |  | Lift Procedure (ENG-021) |
|  | Master Equip. List Mod (GEN-005) |  | ES&H Review (NEPA, IH, etc.) |
|  | RWP (HP-OP-20) |  | Independent Review |
|  | ATI Walkdown |  | Pre-job Brief |
|  | Post-job Brief * |  |  |
| D-Site Specific: |
|  | D-Site Work Permit (OP-AD-09) |  | Door Permit (OP-G-93) |
|  | Tritium Work Permit (OP-AD-49) |  | USQD (OP-AD-63) |
|  | Pre-job brief (OP-AD-79) |  | T-MOD (OP-AD-03) |
|  | ** DCA/DCN (OP-AD-104) #_ |  |  |

* 	Required for installations involving internal vacuum vessel installations, critical lifts, and for the initial installation of repetitive work

**	OP-AD-104 was voided by procedure ENG-032. However, DCAs that were open at the time of adoption of ENG-032 are still considered valid for work approval purposes.

REVIEWERS (designated by RLM)

Accountable Technical Individual

Test Director

Independent Reviewer

D-Site Shift Supervisor

NSTX

TFTR Caretaking

Vacuum

Computer

Tritium

Quality Assurance/Quality Control

AC Power

Maintenance and Operations Division

Energy Conversion System/Motor Control System

Environmental Restoration & Waste Management Division

Water

Neutral Beam (Heating Systems Branch of Electrical Engineering)

Radiofrequency (Heating Systems Branch of Electrical Engineering)

Diagnostics

Environmental, Safety, & Health

| TRAINING (designated by RLM) No training required Instructor |
| --- |
| Personnel (group, job title or individual name) | Read Only | Instruction | Hands-On |
| P. Bisbal | x |  |  |
| T. Carroll | x |  |  |
| B. Davis | x |  |  |
| J. Dong | x |  |  |
| T. Gibney | x |  |  |
| R. Hatcher | x |  |  |
| P. Roney | x |  |  |
| K. Silber | x |  |  |
| J. Wertenbaker | x |  |  |
| C. Neumeyer |  |  |  |
| Training Rep. _______________________________ |  |  |  |
| RLM ______________________________________ |  |  |  |

# Introduction

The NSTX Central Instrumentation & Control (CI&C) system provides remote control, monitoring, data acquisition, and data management for the NSTX.  The system will provide researchers with access to the facility in support of the operation, physics planning, analysis, and coordination of experimental objectives. The CI&C is comprised of six major elements, the Process Control System, Safety System, Network System, Data Acquisition System, Synchronization System, and Plasma Control System.

To improve system reliability, configuration changes must be controlled. This document describes the configuration control policies for the CI&C.

# Purpose

The purpose of this procedure is to:

1.) Define the levels of CONFIGURATION MANAGEMENT required for the CI&C system. This procedure governs all configuration changes made to the CI&C system.

2.) Define the implemented CONTROL MECHANISMS that enable authorized personnel to access the CI&C software.

# Definitions

CI&C Manager:	The individual accountable for the implementation and management of all hardware and software components of the CI&C.

Cognizant Software Engineer (Cog):	The individual assigned the responsibility for a specific set of software. The appendices list the cog's for critical software.

Computer Security Engineer: The individual assigned the responsibility for network and computer security.

Critical Software: Software which is considered critical as determined by the Engineering/Diagnostic Engineer OR Computer System's Division Management.

EPICS: 	Experimental Physics Industrial Control System.  A collection of software used for process control applications on the NSTX CI&C Process Control system.

EPICS System Administrator:	The individual assigned the responsibility for the EPICS software and configuration.

Responsible Line Manager (RLM): The manager who accepts responsibility for the work and process leading to the performance of work.

Routine Work: Low-impact work which is done on a daily or weekly basis by trained individuals.

SCN: Software Change Notice.  This is a procedure within PPPL Engineering Procedure ENG-010 used to document changes to software.

System Engineer:	The individual assigned responsibility for a specific engineering or diagnostic subsystem. Appendix A lists the System Engineers.

# Hardware & Software Configuration Management

- Permanent hardware modifications are subject to the requirements of PPPL Engineering Procedure No. ENG-032, Work Planning Procedure.  No further requirements are imposed by this procedure.

- Temporary hardware modifications to facilitate testing, maintenance, and operations during contingency situations are subject to NSTX Operations Procedure No. OP-AD-03, Control of Temporary Modifications.  No further requirements are imposed by this procedure.

- CI&C software configuration management policies are described in this document.

- PROCEDURE 1:	General System Administration.

- PROCEDURE 2:	Procedure to Change Critical Software.

- PROCEDURE 3:	Procedure to Change Non-Critical

Software.

- The NSTX CI&C software configuration management applies to the following computer systems :

- epicsrv1

- kees

- ppcc

- windex

## PROCEDURE #1: General System Administration

General system administration is a necessary function for any computer system. Examples of system administration functions include security patches, managing user accounts, altering a system-backup schedule, or installing a new software utility.

| Responsibility | Action |
| --- | --- |
| Cog | 1. Advise the CI&C Manager of all computer system administration activities. |

## PROCEDURE #2: Procedure to Change Critical Software

Changes to critical software or non-routine software changes shall follow PPPL Engineering Procedure ENG-010, which will use an SCN to control changes. Note that the Responsible Line Manager is empowered to use procedure ENG-010 to dictate that ENG-032, Work Planning Procedure, be followed.

- Critical NSTX CI&C Software is listed in the appendices of this procedure.

| Responsibility | Action |
| --- | --- |
| Cog | 1. Complete an SCN per PPPL Engineering Procedure ENG-010 |

## PROCEDURE #3: Procedure to Change Non-Critical Software

During the operation of system a System Engineer may discover an error in the software support, or determine the need for additional functionality.

| Responsibility | Action |
| --- | --- |
| System Engineer | Determine the need for a software change and notify the Cog. |
| Cog | Review the System Engineer's information and determine a solution. |

| Cog | Determine course of action: If the required software changes are routine AND no critical software is affected then continue with this Procedure (#3). Otherwise follow this document's Procedure #2, Procedure to Change Critical Software. |
| --- | --- |

| Cog | Obtain the approval of the System Engineer (or designee) to move the revised version of the software 'online'. A computer-reboot may be required to load revised or new software or configurations. Obtain the approval of the D-Site Shift Supervisor prior to rebooting a CI&C computer during periods of active NSTX Operations. |
| --- | --- |
| System Engineer | Evaluate the revised software and advise the cog of the need for additional changes. |

# Control Mechanisms

## Control of Firewall Access

The Process Control portion of the NSTX network system has a firewall installed to protect the engineering subsystems from unauthorized control.  The Computer Security Engineer is responsible for configuring the firewall.

| Responsibility | Action |
| --- | --- |
| Computer Security Engineer | Advise NSTX Engineering Manager of all changes to the firewall rules database. |

## Control of CI&C Computer Passwords

Each user or operator on an NSTX CI&C computer will have a password-protected account which will restrict access to data, control, and configuration capabilities.

## Control of EPICS Operator Passwords

Each engineering subsystem on EPICS will have a password-protected 'operator' account which will restrict access to control capabilities.  The EPICS System Administrator is the only person who has access to all passwords.

| Responsibility | Action |
| --- | --- |
| System Engineer | Request a new 'operator' account or password change. |
| EPICS System Administrator | Implement the request. |

## Control of EPICS Access Security Definition

In addition to the computer user account passwords described above, EPICS provides an additional layer of security, Channel Access Security.  This layer provides a further restriction on an operator’s control-permissions. The System Engineer is responsible for specifying the control permissions for their system.

| Responsibility | Action |
| --- | --- |
| System Engineer | Provide a written request to the EPICS System Administrator to change control permissions. |
| EPICS System Administrator | Implement the request. |

# Appendices

- Appendix A - NSTX System Engineers

- Appendix B - Process Control System Critical Software

- Appendix C - Data Acquisition System Critical Software

- Appendix D - Plasma Control System Critical Software

Appendix A

NSTX System/Diagnostic Engineers & Software ATI

Rev 00 04JAN00 PS  Created by P. Sichta

=======================================================

| Subsystem | DI | System Engineer |
| --- | --- | --- |
| NSTX Clock System | CK | G. Pearson |
| RF Systems | FW | J.R. Wilson |
| Gas Injection | GS | W. Blanchard |
| Motor Generator | MG | M. Awad |
| Neutral Beam | NB | T. Stevenson |
| FCPC | PC | C. Neumeyer |
| Thermocouples | TC | H. Kugel |
| Vacuum | VM | W. Blanchard |

Appendix B

Process Control System Critical Software List

Rev 00 04JAN00 PS  Created by P. Sichta

| Filename | epicsrv1 Directory | Description | Software Cog |
| --- | --- | --- | --- |
| * | /usr/local/epics/system/epics/base | EPICS Base Release | J. Dong |
| * | /usr/wind | vxWorks configuration files and built-kernel | P. Sichta |
| /camac/* | /usr/local/epics/system/epics/epicsExtensions/extensions/src | CAMAC Driver | P. Sichta |
| /stripTool-2-4-b7/* | <same as above> | Current Trending Display Tool | P. Sichta |
| /ss_ar/* | <same as above> | Save Set Archiver | P. Sichta |
| /alh/* | <same as above> | Alarm Handler | P. Sichta |
| /ca/* | <same as above> | Channel Access client calls | P. Sichta |
| medm | /usr/local/epics/system/epics/epicsExtensions/extensions/bin/solaris | Display Manager | J. Dong |
| gdct | <same as above> | Graphical Database Configuration Tool | J. Dong |

| Filename | epicsrv1 Directory | Description | Software Cog |
| --- | --- | --- | --- |
| base.dbd, baseLIBOBJS | /export/home/epics/nstx/epicapps/ceApp/src | database definitions | P. Sichta |
| abDcm*, allenBradley* | <same as above> | AllenBradley PLC support | J. Dong |
| modbus* | <same as above> | Modbus PLC protocol support | P. Sichta |
| camac* | <same as above> | CAMAC device & record support | P. Sichta |
| ppl908Record* | <same as above> | 908 digitizer record support | P. Sichta |
| ce_sub404.c | <same as above> | 404 Timing Module record support | P. Sichta |
| devTimeOfDay.c | <same as above> | TimeStamp device support. | P. Sichta |
| ck_control.st | /export/home/epics/nstx/epicapps/ckApp/src | NSTX Clock Control program | P. Sichta |
| ck_evtCLK.c, ck_ipcsSOC.c | <same as above> | Clock event notification via IPCS | P. Sichta |
| cm_908acq.c | /export/home/epics/nstx/epicapps/cmApp/src | Trans. digitizer acquisition program | P. Sichta |
| /ipcs/*, /PPPL_RES/*, /LLNL_RES/* | /export/home/gibney | IPCS source, makefiles, etc... | T. Gibney |

| Filename | windex Directory | Description | Software Cog |
| --- | --- | --- | --- |
|  |  |  | P. Bisbal |

Appendix C

Data Acquisition System Critical Software List

Rev 00 <date>  <initials>   Created by <name>

| Filename | windex Directory | Description | Software Cog |
| --- | --- | --- | --- |
|  |  |  | P. Roney |

Appendix D

Plasma Control System Critical Software List

Rev 00 <date>  <initials>   Created by <name>

| Filename | ppcc Directory | Description | Software Cog |
| --- | --- | --- | --- |
|  |  |  | T. Gibney |