Startup of the EPICPC01 Computer for NSTX Vacuum System

# ==============================================================

# Rev. 0	22JUN00	P. Sichta

# Rev. 1	29JUN00	PS

==============================================================

# 1.0 Introduction

This procedure provides a description of how to startup the Personal Computer named EPICPC01.  This computer is located in the NSTX Control Room and is used for remote control of the NSTX Vacuum System.  The control program is RSView32 running on the Windows95 operating system.  Reference (a) describes system shutdown.

# 2.0 References

- Shutdown of the EPICPC01 Computer

# 3.0 Procedure

- Verify that the NSTX Engineering Network is operating normally.

- Turn the EPICPC01 computer on using its front-panel power switch.  Do not use the Ctrl-Alt-Del method.

- During the boot sequence a dialog box will appear entitled Network Password Prompt.  Enter a carriage return at this prompt, no networking password is required.

- Note that the NetBackup program may automatically start.

- Start the RSView32 program by poking the mouse on the Start icon on the taskbar, then selecting TVPS_RUNTIME.

- Two windows will appear.  Maximize the window entitled RSView32 Runtime 1500.

- On the other window, entitled with a name similar to        PLC31_M 5-7-98 Project, poke the Run Project button.

- Make a notation in the Vacuum Operations Logbook, located near the computer.