Shutdown of the CI&C Computer System for NSTX Operations

# ==============================================================

# Rev. 00  22DEC99  P. Sichta

Rev. 01  28JUN00  PS

Rev. 02  25JAN01  PS

Rev. 03  11APR01  PS

Rev. 04  08NOV02  PS

==============================================================

## Table of Contents

Introduction

References

Overview

Procedure

# 1.0 Introduction

This procedure provides a description of how to shutdown and power off portions of the NSTX Central Instrumentation & Control (CI&C) system which run EPICS. This procedure does not address the Physics Computing or Network portions of the CI&C.

A description of the major components of the CI&C system are presented below along with a description of how to shutdown each item. The procedure assumes that all hardware is operating normally.  Ref. (b) describes system startup.

# 2.0 References

- IOC Shutdown Procedure

- Startup of the CI&C System for NSTX Operations

# 3.0 Procedure

3.1 EPICS Computers

3.1.1 Host Computer - Solaris Workstations

Note epicsrv is an alias to either epicsrv1 or epicsrv2, and is the computer is supporting NSTX Operations.

# windex

Windex is used as a boot server for the CI&C x-terminals.  This computer managed by the PPLCC operators.  Call them to request a system shutdown.

epicsrv

This computer runs the Solaris operating system.

To shutdown and power-down with a 5-minute warning to user's:

- Login as root from the system console

- /usr/sbin/shutdown -y -g 300 -i 5

The system will automatically shut off its power when this process is complete.  To automatically reboot the system substitute '-i 5'  with '-i 6'.

For immediate shudown, type ‘init 5’ as the root user.

epicsgate01

This computer runs the Solaris operating system. It provides the general user community on non-Engineering/secure networks access to NSTX EPICS points.

Follow the same procedure as for the epicsrv computer.

NSTXPC09

This computer runs the Windows operating system. It provides the general user community on non-Engineering/secure networks viewing access to NSTX data points via LabVIEW displays.

Shutdown the computer in the normal WINDOWS fashion.  You will need the NSTX EPICS cicopr account password.

3.1.2 IOC - Input/Output Controllers

Shutdown all IOC  according to the IOC Shutdown Procedure (ref. (a)).

3.1.3 OPI - Operator Display Stations

To power-off an x-terminal, turn the power switch to the OFF position.  This is usually on the left back corner of the base unit.

3.2 Communications Links

Communication link transmitter and receivers for RS-232 or PLC communications should be unplugged from their power sources.

3.3 CAMAC Links

CAMAC crates should be switched off.

3.4 NSTX Control Room Equipment List

The list below shows the CI&C Equipment in the NSTX Control Room.

| Equipment Classification | Item | Procedure ? |
| --- | --- | --- |
| NSTX Engineering Computing | epicsrv1 & disk | Y |
|  | epicsrv2 & disk | Y |
|  | epicioc1 | Y |
|  | epicioc9 | Y |
|  | epicsgate01 | Y |
|  | NSTXPC09 | Y |
|  | IOC console PC |  |
|  | Vacuum PC | Y |
|  | RGA PC (2) | Y |
|  | X-terminals |  |
|  | Laser Printer |  |
|  | development PLC |  |
|  | development CAMAC crate |  |
|  | Pilkington RS-232 |  |
|  | RS-232 optic Mux |  |
|  | Rack 100 CAMAC Crate |  |
|  | HP Mux#3C in Rack 100 |  |
|  | Clock Rack, Timing Crate |  |
|  | HSDL crate |  |
| NSTX Physics Computing | Kees & Disk Array |  |
|  | Luna |  |
|  | MEL & local crate & Driver |  |
|  | CAMAC Highway Drivers |  |
|  | CAMAC crates |  |
|  | Laser Printer |  |
|  | X-terminals |  |
|  | MACs |  |
| NSTX Network Equipment | Engineering HUB/Switch | no action req'd (auto-restart) |
|  | Physics HUB/Switch | no action req'd (auto-restart) |
| TRECAMS | OCM | Y |
|  | Line Printer |  |
|  | Color Hardopy |  |
|  | Laser Printer |  |
|  | CDCM | Y |
| LINX (Security) | Linx Panel #2 | no action req'd (UPS) |