# CI&C Data Acquisition User Guide

# Rev  0  10AUG99  P. Sichta

# Rev  1  26AUG99  P. Sichta

# Rev  2  21AUG00  P. Sichta

# 1.0 Introduction

This document will describe how to configure the Data Acquisition for the CI&C system.

Revision 2 describes the changes to acquisition to support multiple CAMAC links.

# 2.0 References

N/A

# 3.0 Overview

Following an NSTX shot a Data Acquisition process will read waveforms stored in CAMAC memory modules along with parameters associated with the digitized signal (name, scaling, etc...).  The data is then compiled into a file that is sent to computers on the NSTX Physics Network.  The computer (KEES) will store the data in a predefined MDSplus data tree. At this time only 908/3232 transient digitizers are acquired.

Normally two file types need to be configured to specify which digitizers will be archived to MDSplus after each shot:

- Master file

- Active file

# 4.0 Configuration

Data Acquisition is driven by a number of ascii files.  These can be edited with any text editor.  Three file types are used, one Master file, one Active file, and a number of Digitizer files.  There is one set of files for each CAMAC link. The files are each described below.

## 4.1 Master File

The first file to configure is the Master file. There is one Master File for each CAMAC link. This is a one-line file which contains (only) the name of an Active file (described in next section).  The Active filename must include its' absolute path. Figure 1 shows an example Master file.  Figure 1 also shows the ChangeLog file which should be used to record changes to the Master files.

The Master file must be named cm_X908acq_master.cfg and must be in the directory /nstx/epicapps/cmApp/op/rdt.  Note there is a symbolic link from the root directory for /nstx.

The 'X' in the filename is a character to designate which CAMAC link the Master File is used for:

- X=A,  CAMAC Link EPICS_1

- X=B,  CAMAC Link EPICS_2

- X=C,  CAMAC Link EPICS_3

## 4.2 Active File

The next file to configure is the Active file. The Active file contains a list of filenames (with absolute paths) for one or more Digitizer files. Figure 2 shows an example Active file. The Active file that is listed in the Master file will be used by Data Acquisition.

By convention the Active file should use a .cfg suffix and should reside in the directory /nstx/epicapps/cmApp/op/rdt.

## 4.3 Digitizer File

Normally the Digitizer file is created by the EPICS Application Developer when a new digitizer is added to the CAMAC system. If acquisition is desired, this file must be listed in the Active file.

By convention the Digitizer file should use a .lst suffix. Digitizer files reside in the subsystem's directory /nstx/epicapps/xxApp/op/rdt.  xx is the digraph of the subsystem.  Figure 3 shows a typical Digitizer file.

    - Digitizer File Format

Digitizer files contain three classes of items.  Comment lines begin with the '#' character. The second class is the Target filename.  This is the filename root of the file which will be written to the epicsrv1 /data/nstx908 directory.  The acquisition program will then copy the file to the Physics Network computer (KEES) disk directory /kees1/epics_temp.  By convention,  there is one file per digitizer and the filename indicates the subsystem digraph, crate number and slot number.  The third class of information in the Digitizer file is a list of EPICS record names.  These names must be of record type ppl908.

## 5.0 Data Acquisition Monitoring

Data Acquisition can be monitored using medm display page CM05 and CM06.  Figures 4 and 5 shows these pages.

## Figure 1 – Sample Master file and ChangeLog

/export/home/epics/nstx/epicapps/cmApp/op/rdt :ls

ChangeLog             cm_acqTest.cfg        cm_acq_3.cfg

README                cm_acq_1.cfg          cm_acq_GS.cfg

cm_908acq_master.cfg  cm_acq_2.cfg          cm_acq_PC.cfg

/export/home/epics/nstx/epicapps/cmApp/op/rdt :

/export/home/epics/nstx/epicapps/cmApp/op/rdt :

/export/home/epics/nstx/epicapps/cmApp/op/rdt :more cm_908acq_master.cfg

/export/home/epics/nstx/epicapps/cmApp/op/rdt/cm_acqTest.cfg

/export/home/epics/nstx/epicapps/cmApp/op/rdt :

/export/home/epics/nstx/epicapps/cmApp/op/rdt :more ChangeLog

This ascii file will be used to record changes to the master configuration file

.

DATE    CHANGE

----

----    ---------------------------------------------------

04AUG99 Changed from cm_acqNONE.cfg to cm_acq_GS.cfg.

Deleted cm_acqNONE.cfg

06AUG99 Changed master list from cm_acq_GS.cfg to cm_acq_1.cfg

09AUG99 Changed master list from cm_acq_1.cfg to cm_acq_GS.cfg

10AUG99 Changed master list from cm_acq_GS.cfg to cm_acqTest.cfg

#

/export/home/epics/nstx/epicapps/cmApp/op/rdt :

## Figure 2 – Sample Active File

/export/home/epics/nstx/epicapps/cmApp/op/rdt :ls

ChangeLog             cm_acqTest.cfg        cm_acq_3.cfg

README                cm_acq_1.cfg          cm_acq_GS.cfg

cm_908acq_master.cfg  cm_acq_2.cfg          cm_acq_PC.cfg

/export/home/epics/nstx/epicapps/cmApp/op/rdt :more cm_acq_1.cfg

# 908 Acquisition Configuration file  cm_acq_1

#

#  created 28JAN99 by P. Sichta

#  rev 1 24FEB99  PS  added c18n02

#  rev 2 22MAR99  PS  removed one c01n17.  it was listed twice.

#  rev 3 29APR99  PS  added 17/4,9,17 & 22/14

#

# This file will hold a list of .lst files,  which will hold ppl908 record

#   names for acquisition.  There will be an rdt file for each .lst file

#

/export/home/epics/nstx/epicapps/pcApp/op/rdt/pc_908c16n03.lst

/export/home/epics/nstx/epicapps/pcApp/op/rdt/pc_908c16n08.lst

/export/home/epics/nstx/epicapps/pcApp/op/rdt/pc_908c22n05.lst

/export/home/epics/nstx/epicapps/pcApp/op/rdt/pc_908c22n09.lst

/export/home/epics/nstx/epicapps/pcApp/op/rdt/pc_908c01n17.lst

/export/home/epics/nstx/epicapps/pcApp/op/rdt/pc_908c10n17.lst

/export/home/epics/nstx/epicapps/pcApp/op/rdt/pc_908c20n02.lst

/export/home/epics/nstx/epicapps/pcApp/op/rdt/pc_908c19n02.lst

/export/home/epics/nstx/epicapps/pcApp/op/rdt/pc_908c21n02.lst

/export/home/epics/nstx/epicapps/pcApp/op/rdt/pc_908c12n17.lst

/export/home/epics/nstx/epicapps/pcApp/op/rdt/pc_908c04n18.lst

/export/home/epics/nstx/epicapps/pcApp/op/rdt/pc_908c05n18.lst

/export/home/epics/nstx/epicapps/pcApp/op/rdt/pc_908c18n02.lst

/export/home/epics/nstx/epicapps/gsApp/op/rdt/gs_908c28n14.lst

/export/home/epics/nstx/epicapps/pcApp/op/rdt/pc_908c17n04.lst

/export/home/epics/nstx/epicapps/pcApp/op/rdt/pc_908c17n09.lst

/export/home/epics/nstx/epicapps/pcApp/op/rdt/pc_908c17n17.lst

/export/home/epics/nstx/epicapps/pcApp/op/rdt/pc_908c22n14.lst

/export/home/epics/nstx/epicapps/cmApp/op/rdt :

## Figure 3 – Sample Digitizer File

/export/home/epics/nstx/epicapps/pcApp/op/rdt :ls

pc_908c01n17.lst   pc_908c16n08.lst   pc_908c17n17.lst%  pc_908c22n09.lst

pc_908c04n18.lst   pc_908c17n04.lst   pc_908c18n02.lst   pc_908c22n14.lst

pc_908c05n18.lst   pc_908c17n04.lst%  pc_908c19n02.lst   pc_908c22n19.lst

pc_908c10n17.lst   pc_908c17n09.lst   pc_908c20n02.lst

pc_908c12n17.lst   pc_908c17n09.lst%  pc_908c21n02.lst

pc_908c16n03.lst   pc_908c17n17.lst   pc_908c22n05.lst

/export/home/epics/nstx/epicapps/pcApp/op/rdt :more pc_908c17n17.lst

# file pc_908c17n17.lst

# created 28APR99 by P. Sichta

# Revised 04AUG99 by P. Sichta

#               Added pc_plasma_cur2f and changed pc_plasma_curf to

#               pc_plasma_cur_1f

#

# This file will hold a list of ppl908 record names which must be in the

#  same 908.

# This file is called by a .cfg file in the CM op/rdt directory

# An rdt file will be created from this .lst file.

#

#  The form of the TARGET must be XX_908cYYnZZ

### TARGET_FILE pc_908c17n17

pc_pf3l_br_2_cur_1f

pc_pf3u_br_2_cur_1f

pc_chi_br_2_cur_1f

pc_chi_br_1_cur_1f

pc_mg_speedf

pc_mg_voltagef

pc_mg_currentf

pc_plasma_cur_1f

pc_dummy_load_curf

pc_tf_tot_curf

pc_oh_tot_curf

pc_plasma_cur2f

/export/home/epics/nstx/epicapps/pcApp/op/rdt :

Figure 4 – Display CM05

Figure 5 – Display CM06