| CRATE LAYOUT DESCRIPTION |  |
| --- | --- |

| SLOT | CROSS-CX | MODULE DESCRIPTION & STRAPPING |
| --- | --- | --- |
| NSTX 1 | A01 - A16 | 322 16-BIT DIGITAL INPUT MODULE - ISOLATED CONTACT |
| NSTX 2 | A17 - A32 | 322 16-BIT DIGITAL INPUT MODULE - ISOLATED CONTACT |
| NSTX 3 | A33 - A48 | 322 16-BIT DIGITAL INPUT MODULE - ISOLATED CONTACT |
| NSTX 4 | A49 - A64 | 322 16-BIT DIGITAL INPUT MODULE - ISOLATED CONTACT |
| NSTX 5 | A65 - A80 | 322 16-BIT DIGITAL INPUT MODULE - ISOLATED CONTACT |
| NSTX 6 | B01 - B16 | 322 16-BIT DIGITAL INPUT MODULE - ISOLATED CONTACT |
| NSTX 7 | B17 - B32 | 322 16-BIT DIGITAL INPUT MODULE - ISOLATED CONTACT |
| NSTX 8 | B33 - B48 | 322 16-BIT DIGITAL INPUT MODULE - ISOLATED CONTACT |
| NSTX 9 | B49 - B64 | 322 16-BIT DIGITAL INPUT MODULE - ISOLATED CONTACT |
| 10 | B65 - B80 | 322 16-BIT DIGITAL INPUT MODULE - ISOLATED CONTACT |
| NSTX 11 | D01 - D16 | 322 16-BIT DIGITAL INPUT MODULE - ISOLATED CONTACT |
| NSTX 12 | D17 - D32 | 16-BIT DIGITAL OUTPUT MODULE - 302 RELAY OUTPUTS, MOMENTARY, NORM OPEN |
| NSTX 13 | D33 - D48 | 16-BIT DIGITAL OUTPUT MODULE - 302 RELAY OUTPUTS, MOMENTARY, NORM OPEN |
| NSTX 14 | D49 - D64 | 16-BIT DIGITAL OUTPUT MODULE - 302 RELAY OUTPUTS, MOMENTARY, NORM OPEN |
| NSTX 15 | D65 - D80 | 16-BIT DIGITAL OUTPUT MODULE - 302 RELAY OUTPUTS, MOMENTARY, NORM OPEN |
| 16 | C01 - C16 | 322 16-BIT DIGITAL INPUT MODULE - ISOLATED CONTACT |
| 17 | C17 - D32 | 322 16-BIT DIGITAL INPUT MODULE - ISOLATED CONTACT |
| 18 | C33 - C48 | 322 16-BIT DIGITAL INPUT MODULE - ISOLATED CONTACT |
| 19 | C49 - C64 | 322 16-BIT DIGITAL INPUT MODULE - ISOLATED CONTACT |
| NSTX 20 | ---- | --- 5 Volt Power for Teledyne Solid State Relays |
| 21 | E01 - E16 | 322 16-BIT DIGITAL INPUT MODULE - ISOLATED CONTACT |
| 22 | E17 - E32 | 322 16-BIT DIGITAL INPUT MODULE - ISOLATED CONTACT |
| 23 | ---- | 313 U-PORT ADAPTER (& FACILITY CLOCK) |
| 24/25 | ---- | 3952 L-2 CRATE CONTROLLER |

| SLOT NO.: 01 | MODULE TYPE 322 DIGITAL INPUT |
| --- | --- |

| SIGNAL NAME | DEVICE ID | CONT. DWG | CROSS |  | CLR | PIN# | CH |
| --- | --- | --- | --- | --- | --- | --- | --- |
| SDS STATS FOR EF1 CONVERTER: BIT 0 | EPFC-MODE-A/B |  | A1 | F B | BRN TAN | 1B 1A | 1 |
| BIT 1 | EPFC-MODE-A/B |  | A2 | F B | RED TAN | 2B 2A | 2 |
|  |  |  | A3 | F B | ORN TAN | 3B 3A | 3 |
|  |  |  | A4 | F B | YLW TAN | 4B 4A | 4 |
| SDS STATS FOR EF1 CONVERTER: 1 = CONTROL POWER ON | EEF1-CBD-EF1 | B-4F1005 SH. 1030 | A5 | F B | GRN TAN | 5B 5A | 5 |
| SDS STATS FOR OH4 CONVERTER: 1 = CONTROL READY | EOH4-SDS-D1 | B-4F1005 SH. 672 | A6 | F B | BLU TAN | 6B 6A | 6 |
| 1 = DOORS CLOSED | EOH4-SDS-D1 | B-4F1005 SH. 672 | A7 | F B | VIO TAN | 7B 7A | 7 |
| 1 = GROUNDING SWITCH CLOSED | EOH4-SDS-D1 | B-4F1005 SH. 672 | A8 | F B | GRY TAN | 8B 8A | 8 |
| 1 = GROUNDING SWITCH OPEN | EOH4-SDS-D1 | B-4F1005 SH. 672 | A9 | F B | BRN TAN | 9B 9A | 9 |
| 1 = LINE SWITCH CLOSED | EOH4-SDS-D1 | B-4F1005 SH. 672 | A10 | F B | RED TAN | 10B 10A | 10 |
| 1 = LINE SWITCH OPEN | EOH4-SDS-D1 | B-4F1005 SH. 672 | A11 | F B | ORN TAN | 11B 11A | 11 |
| 0 = BUS LINK NOT NORMAL | EOH4-SDS-D1 | B-4F1005 SH. 672 | A12 | F B | YLW TAN | 12B 12A | 12 |
| 1 = BUS LINK REVERSED | EOH4-SDS-D1 | B-4F1005 SH. 672 | A13 | F B | GRN TAN | 13B 13A | 13 |
| 1 = BUS LINK NOT IN BYPASS POSITION | EOH4-SDS-D1 | B-4F1005 SH. 672 | A14 | F B | BLU TAN | 14B 14A | 14 |
| 1 = BUS LINK IN BYPASS POSITION | EOH4-SDS-D1 | B-4F1005 SH. 672 | A15 | F B | VIO TAN | 15B 15A | 15 |
| 1 = AIR PRESSURE LOW | EOH4-SDS-D1 | B-4F1005 SH. 672 | A16 | F B | GRY TAN | 16B 16A | 16 |

| SLOT NO.: 02 | MODULE TYPE 322 DIGITAL INPUT |
| --- | --- |

| SIGNAL NAME | DEVICE ID | CONT. DWG | CROSS |  | CLR | PIN# | CH |
| --- | --- | --- | --- | --- | --- | --- | --- |
| SDS STATS FOR TF2 CONVERTER: 1 = DOORS CLOSED | ETF2-SDS-D2 NSTX OH | B-4F1005 SH. 1021 | A17 | F B | BRN TAN | 1B 1A | 1 |
| 1 = GROUNDING SWITCH CLOSED | ETF2-SDS-D2 NSTX OH | B-4F1005 SH. 1021 | A18 | F B | RED TAN | 2B 2A | 2 |
| 1 = GROUNDING SWITCH OPEN | ETF2-SDS-D2 NSTX OH | B-4F1005 SH. 1021 | A19 | F B | ORN TAN | 3B 3A | 3 |
| 1 = LINE SWITCH 1 CLOSED | ETF2-SDS-D2 NSTX OH | B-4F1005 SH. 1021 | A20 | F B | YLW TAN | 4B 4A | 4 |
| 1 = LINE SWITCH 1 OPEN | ETF2-SDS-D2 NSTX OH | B-4F1005 SH. 1021 | A21 | F B | GRN TAN | 5B 5A | 5 |
| 1 = LINE SWITCH 2 CLOSED | ETF2-SDS-D2 NSTX OH | B-4F1005 SH. 1021 | A22 | F B | BLU TAN | 6B 6A | 6 |
| 1 = LINE SWITCH 2 OPEN | ETF2-SDS-D2 NSTX OH | B-4F1005 SH. 1021 | A23 | F B | VIO TAN | 7B 7A | 7 |
| 1 = LINE SWITCH 3 CLOSED | ETF2-SDS-D2 NSTX spare | B-4F1005 SH. 1021 | A24 | F B | GRY TAN | 8B 8A | 8 |
| 1 = LINE SWITCH 3 OPEN | ETF2-SDS-D2 NSTX spare | B-4F1005 SH. 1021 | A25 | F B | BRN TAN | 9B 9A | 9 |
| 1 = LINE SWITCH 4 CLOSED | ETF2-SDS-D2 NSTX RWM | B-4F1005 SH. 1021 | A26 | F B | RED TAN | 10B 10A | 10 |
| 1 = LINE SWITCH 4 OPEN | ETF2-SDS-D2 NSTX RWM | B-4F1005 SH. 1021 | A27 | F B | ORN TAN | 11B 11A | 11 |
| 0 = BRANCH 1 BUS LINK NOT NORMAL | ETF2-SDS-D2 NSTX OH-1 | B-4F1005 SH. 1021 | A28 | F B | YLW TAN | 12B 12A | 12 |
| 1 = BRANCH 1 BUS LINK REVERSED | ETF2-SDS-D2 NSTX OH-1 | B-4F1005 SH. 1021 | A29 | F B | GRN TAN | 13B 13A | 13 |
| 0 = BRANCH 2 BUS LINK NOT NORMAL | ETF2-SDS-D2 NSTX OH-2 | B-4F1005 SH. 1021 | A30 | F B | BLU TAN | 14B 14A | 14 |
| 1 = BRANCH 2 BUS LINK REVERSED | ETF2-SDS-D2 NSTX OH-2 | B-4F1005 SH. 1021 | A31 | F B | VIO TAN | 15B 15A | 15 |
| SDS STATS FOR TF2 CONVERTER: 1 = CONTROL POWER ON | ETF2-CBD-TF2 | B-4F1005 SH. 1030 | A32 | F B | GRY TAN | 16B 16A | 16 |

| SLOT NO.: 03 | MODULE TYPE 322 DIGITAL INPUT |
| --- | --- |

| SIGNAL NAME | DEVICE ID | CONT. DWG | CROSS |  | CLR | PIN# | CH |
| --- | --- | --- | --- | --- | --- | --- | --- |
| TF2 SDS STATUS : 0 = BRANCH 3 BUS LINK NOT NORMAL | ETF2-SDS-D3 NSTX spare | B-4F1005 SH. 1021 | A33 | F B | BRN TAN | 1B 1A | 1 |
| 1 = BRANCH 3 BUS LINK REVERSED | ETF2-SDS-D3 NSTX spare | B-4F1005 SH. 1021 | A34 | F B | RED TAN | 2B 2A | 2 |
| 0 = BRANCH 4 BUS LINK NOT NORMAL | ETF2-SDS-D3 NSTX RWM | B-4F1005 SH. 1021 | A35 | F B | ORN TAN | 3B 3A | 3 |
| 1 = BRANCH 4 BUS LINK REVERSED | ETF2-SDS-D3 NSTX RWM | B-4F1005 SH. 1021 | A36 | F B | YLW TAN | 4B 4A | 4 |
| SDS STATS FOR OH4 CONVERTER: 1 = AIR PRESSURE LOW | ETF2-SDS-D1 NSTX OH | B-4F1005 SH. 1021 | A37 | F B | GRN TAN | 5B 5A | 5 |
| 1 = CONTROL READY | ETF2-SDS-D1 NSTX OH | B-4F1005 SH. 1021 | A38 | F B | BLU TAN | 6B 6A | 6 |
| SDS STATUS FOR HF CONVERTER: 1 = CONTROL READY | EHF-SDS-D1 | B-4F1005 SH. 581 | A39 | F B | VIO TAN | 7B 7A | 7 |
| 1 = DOORS CLOSED | EHF-SDS-D1 | B-4F1005 SH. 581 | A40 | F B | GRY TAN | 8B 8A | 8 |
| 1 = GROUNDING SWITCH CLOSED | EHF-SDS-D1 | B-4F1005 SH. 581 | A41 | F B | BRN TAN | 9B 9A | 9 |
| 1 = GROUNDING SWITCH OPEN | EHF-SDS-D1 | B-4F1005 SH. 581 | A42 | F B | RED TAN | 10B 10A | 10 |
| 1 = LINE SWITCH CLOSED | EHF-SDS-D1 | B-4F1005 SH. 581 | A43 | F B | ORN TAN | 11B 11A | 11 |
| 1 = LINE SWITCH OPEN | EHF-SDS-D1 | B-4F1005 SH. 581 | A44 | F B | YLW TAN | 12B 12A | 12 |
| 1 = AIR PRESSURE LOW | EHF-SDS-D1 | B-4F1005 SH. 581 | A45 | F B | GRN TAN | 13B 13A | 13 |
|  |  |  | A46 | F B | BLU TAN | 14B 14A | 14 |
|  |  |  | A47 | F B | VIO TAN | 15B 15A | 15 |
|  |  |  | A48 | F B | GRY TAN | 16B 16A | 16 |

| SLOT NO.: 04 | MODULE TYPE 322 DIGITAL INPUT |
| --- | --- |

| SIGNAL NAME | DEVICE ID | CONT. DWG | CROSS |  | CLR | PIN# | CH |
| --- | --- | --- | --- | --- | --- | --- | --- |
| SDS STATUS FOR FOH SHARED COIL: 1 = CONTROL READY | EFOH-SDS-D1 | B-4F1005 SH. 420 | A49 | F B | BRN TAN | 1B 1A | 1 |
| 1 = DOORS CLOSED | EFOH-SDS-D1 | B-4F1005 SH. 420 | A50 | F B | RED TAN | 2B 2A | 2 |
| 1 = GROUNDING SWITCH CLOSED | EFOH-SDS-D1 NSTX RWM | B-4F1005 SH. 420 | A51 | F B | ORN TAN | 3B 3A | 3 |
| 1 = GROUNDING SWITCH OPEN | EFOH-SDS-D1 NSTX RWM | B-4F1005 SH. 420 | A52 | F B | YLW TAN | 4B 4A | 4 |
| 0 = EF BYPASSED - "A" MODE | EFOH-SDS-D1 | B-4F1005 SH. 420 | A53 | F B | GRN TAN | 5B 5A | 5 |
| 0 = EF NOT BYPASSED - "B" MODE | EFOH-SDS-D1 | B-4F1005 SH. 420 | A54 | F B | BLU TAN | 6B 6A | 6 |
| 0 = OH NOT BYPASSED - "A" MODE | EFOH-SDS-D1 | B-4F1005 SH. 420 | A55 | F B | VIO TAN | 7B 7A | 7 |
| 0 = OH BYPASSED - "B" MODE | EFOH-SDS-D1 | B-4F1005 SH. 420 | A56 | F B | GRY TAN | 8B 8A | 8 |
| 0 = LINE SWITCH OPEN TO EF - "A" MODE | EFOH-SDS-D1 | B-4F1005 SH. 420 | A57 | F B | BRN TAN | 9B 9A | 9 |
| 0 = LINE SWITCH CLOSED TO EF - "B" MODE | EFOH-SDS-D1 | B-4F1005 SH. 420 | A58 | F B | RED TAN | 10B 10A | 10 |
| 0 = LINE SWITCH CLOSED TO OH - "A" MODE | EFOH-SDS-D1 | B-4F1005 SH. 420 | A59 | F B | ORN TAN | 11B 11A | 11 |
| 0 = LINE SWITCH OPEN TO OH - "B" MODE | EFOH-SDS-D1 | B-4F1005 SH. 420 | A60 | F B | YLW TAN | 12B 12A | 12 |
| 0 = OH 6 COILS IN - "A" MODE | EFOH-SDS-D1 | B-4F1005 SH. 420 | A61 | F B | GRN TAN | 13B 13A | 13 |
| 0 = OH 6 COILS NOT IN - "B" MODE | EFOH-SDS-D1 | B-4F1005 SH. 420 | A62 | F B | BLU TAN | 14B 14A | 14 |
| 1 = AIR PRESSURE LOW | EFOH-SDS-D1 NSTX RWM | B-4F1005 SH. 420 | A63 | F B | VIO TAN | 15B 15A | 15 |
|  |  |  | A64 | F B | GRY TAN | 16B 16A | 16 |

| SLOT NO.: 05 | MODULE TYPE 322 DIGITAL INPUT |
| --- | --- |

| SIGNAL NAME | DEVICE ID | CONT. DWG | CROSS |  | CLR | PIN# | CH |
| --- | --- | --- | --- | --- | --- | --- | --- |
| SDS STATS FOR EF1 CONVERTER: 1 = CONTROL READY | EEF1-SDS-D1 | B-4F1005 SH. 419 | A65 | F B | BRN TAN | 1B 1A | 1 |
| 1 = DOORS CLOSED | EEF1-SDS-D1 | B-4F1005 SH. 419 | A66 | F B | RED TAN | 2B 2A | 2 |
| 1 = GROUNDING SWITCH CLOSED | EEF1-SDS-D1 | B-4F1005 SH. 419 | A67 | F B | ORN TAN | 3B 3A | 3 |
| 1 = GROUNDING SWITCH OPEN | EEF1-SDS-D1 | B-4F1005 SH. 419 | A68 | F B | YLW TAN | 4B 4A | 4 |
| 1 = LINE SWITCH CLOSED | EEF1-SDS-D1 | B-4F1005 SH. 419 | A69 | F B | GRN TAN | 5B 5A | 5 |
| 1 = LINE SWITCH OPEN | EEF1-SDS-D1 | B-4F1005 SH. 419 | A70 | F B | BLU TAN | 6B 6A | 6 |
| 0 = BUS LINK NOT NORMAL | EEF1-SDS-D1 | B-4F1005 SH. 419 | A71 | F B | VIO TAN | 7B 7A | 7 |
| 1 = BUS LINK REVERSED | EEF1-SDS-D1 | B-4F1005 SH. 419 | A72 | F B | GRY TAN | 8B 8A | 8 |
| 1 = BUS LINK NOT IN BYPASS POSITION | EEF1-SDS-D1 | B-4F1005 SH. 419 | A73 | F B | BRN TAN | 9B 9A | 9 |
| 1 = BUS LINK IN BYPASS POSITION | EEF1-SDS-D1 | B-4F1005 SH. 419 | A74 | F B | RED TAN | 10B 10A | 10 |
| 1 = AIR PRESSURE LOW | EEF1-SDS-D1 | B-4F1005 SH. 419 | A75 | F B | ORN TAN | 11B 11A | 11 |
|  |  |  | A76 | F B | YLW TAN | 12B 12A | 12 |
|  |  |  | A77 | F B | GRN TAN | 13B 13A | 13 |
|  |  |  | A78 | F B | BLU TAN | 14B 14A | 14 |
|  |  |  | A79 | F B | VIO TAN | 15B 15A | 15 |
| VC UV (EF4 CONVERTER) : BIT 0 | EPC-XT-UV1 | B-4F1005 SH. 1087 | A80 | F B | GRY TAN | 16B 16A | 16 |

| SLOT NO.: 06 | MODULE TYPE 322 DIGITAL INPUT |
| --- | --- |

| SIGNAL NAME | DEVICE ID | CONT. DWG | CROSS |  | CLR | PIN# | CH |
| --- | --- | --- | --- | --- | --- | --- | --- |
| SDS STATS FOR EF2 CONVERTER: 1 = CONTROL READY | EEF2-SDS-D1 | B-4F1005 SH. 454 | B1 | F B | BRN TAN | 1B 1A | 1 |
| 1 = DOORS CLOSED | EEF2-SDS-D1 | B-4F1005 SH. 454 | B2 | F B | RED TAN | 2B 2A | 2 |
| 1 = GROUNDING SWITCH CLOSED | EEF2-SDS-D1 | B-4F1005 SH. 454 | B3 | F B | ORN TAN | 3B 3A | 3 |
| 1 = GROUNDING SWITCH OPEN | EEF2-SDS-D1 | B-4F1005 SH. 454 | B4 | F B | YLW TAN | 4B 4A | 4 |
| 1 = LINE SWITCH CLOSED | EEF2-SDS-D1 | B-4F1005 SH. 454 | B5 | F B | GRN TAN | 5B 5A | 5 |
| 1 = LINE SWITCH OPEN | EEF2-SDS-D1 | B-4F1005 SH. 454 | B6 | F B | BLU TAN | 6B 6A | 6 |
| 0 = BUS LINK NOT NORMAL | EEF2-SDS-D1 | B-4F1005 SH. 454 | B7 | F B | VIO TAN | 7B 7A | 7 |
| 1 = BUS LINK REVERSED | EEF2-SDS-D1 | B-4F1005 SH. 454 | B8 | F B | GRY TAN | 8B 8A | 8 |
| 1 = BUS LINK NOT IN BYPASS POSITION | EEF2-SDS-D1 | B-4F1005 SH. 454 | B9 | F B | BRN TAN | 9B 9A | 9 |
| 1 = BUS LINK IN BYPASS POSITION | EEF2-SDS-D1 | B-4F1005 SH. 454 | B10 | F B | RED TAN | 10B 10A | 10 |
| 1 = AIR PRESSURE LOW | EEF2-SDS-D1 | B-4F1005 SH. 454 | B11 | F B | ORN TAN | 11B 11A | 11 |
|  |  |  | B12 | F B | YLW TAN | 12B 12A | 12 |
|  |  |  | B13 | F B | GRN TAN | 13B 13A | 13 |
|  |  |  | B14 | F B | BLU TAN | 14B 14A | 14 |
|  |  |  | B15 | F B | VIO TAN | 15B 15A | 15 |
|  |  |  | B16 | F B | GRY TAN | 16B 16A | 16 |

| SLOT NO.: 07 | MODULE TYPE 322 DIGITAL INPUT |
| --- | --- |

| SIGNAL NAME | DEVICE ID | CONT. DWG | CROSS |  | CLR | PIN# | CH |
| --- | --- | --- | --- | --- | --- | --- | --- |
| SDS STATS FOR OH1 CONVERTER: 1 = CONTROL READY | EOH1-SDS-D1 | B-4F1005 SH. 631 | B17 | F B | BRN TAN | 1B 1A | 1 |
| 1 = DOORS CLOSED | EOH1-SDS-D1 | B-4F1005 SH. 631 | B18 | F B | RED TAN | 2B 2A | 2 |
| 1 = GROUNDING SWITCH CLOSED | EOH1-SDS-D1 | B-4F1005 SH. 631 | B19 | F B | ORN TAN | 3B 3A | 3 |
| 1 = GROUNDING SWITCH OPEN | EOH1-SDS-D1 | B-4F1005 SH. 631 | B20 | F B | YLW TAN | 4B 4A | 4 |
| 1 = LINE SWITCH CLOSED | EOH1-SDS-D1 | B-4F1005 SH. 631 | B21 | F B | GRN TAN | 5B 5A | 5 |
| 1 = LINE SWITCH OPEN | EOH1-SDS-D1 | B-4F1005 SH. 631 | B22 | F B | BLU TAN | 6B 6A | 6 |
| 0 = BUS LINK NOT NORMAL | EOH1-SDS-D1 | B-4F1005 SH. 631 | B23 | F B | VIO TAN | 7B 7A | 7 |
| 1 = BUS LINK REVERSED | EOH1-SDS-D1 | B-4F1005 SH. 631 | B24 | F B | GRY TAN | 8B 8A | 8 |
| 1 = BUS LINK NOT IN BYPASS POSITION | EOH1-SDS-D1 | B-4F1005 SH. 631 | B25 | F B | BRN TAN | 9B 9A | 9 |
| 1 = BUS LINK IN BYPASS POSITION | EOH1-SDS-D1 | B-4F1005 SH. 631 | B26 | F B | RED TAN | 10B 10A | 10 |
| 1 = AIR PRESSURE LOW | EOH1-SDS-D1 | B-4F1005 SH. 631 | B27 | F B | ORN TAN | 11B 11A | 11 |
|  |  |  | B28 | F B | YLW TAN | 12B 12A | 12 |
|  |  |  | B29 | F B | GRN TAN | 13B 13A | 13 |
|  |  |  | B30 | F B | BLU TAN | 14B 14A | 14 |
|  |  |  | B31 | F B | VIO TAN | 15B 15A | 15 |
|  |  |  | B32 | F B | GRY TAN | 16B 16A | 16 |

| SLOT NO.: 08 | MODULE TYPE 322 DIGITAL INPUT |
| --- | --- |

| SIGNAL NAME | DEVICE ID | CONT. DWG | CROSS |  | CLR | PIN# | CH |
| --- | --- | --- | --- | --- | --- | --- | --- |
| SDS STATS FOR OH2 CONVERTER: 1 = CONTROL READY | EOH2-SDS-D1 | B-4F1005 SH. 632 | B33 | F B | BRN TAN | 1B 1A | 1 |
| 1 = DOORS CLOSED | EOH2-SDS-D1 | B-4F1005 SH. 632 | B34 | F B | RED TAN | 2B 2A | 2 |
| 1 = GROUNDING SWITCH CLOSED | EOH2-SDS-D1 | B-4F1005 SH. 632 | B35 | F B | ORN TAN | 3B 3A | 3 |
| 1 = GROUNDING SWITCH OPEN | EOH2-SDS-D1 | B-4F1005 SH. 632 | B36 | F B | YLW TAN | 4B 4A | 4 |
| 1 = LINE SWITCH CLOSED | EOH2-SDS-D1 | B-4F1005 SH. 632 | B37 | F B | GRN TAN | 5B 5A | 5 |
| 1 = LINE SWITCH OPEN | EOH2-SDS-D1 | B-4F1005 SH. 632 | B38 | F B | BLU TAN | 6B 6A | 6 |
| 0 = BUS LINK NOT NORMAL | EOH2-SDS-D1 | B-4F1005 SH. 632 | B39 | F B | VIO TAN | 7B 7A | 7 |
| 1 = BUS LINK REVERSED | EOH2-SDS-D1 | B-4F1005 SH. 632 | B40 | F B | GRY TAN | 8B 8A | 8 |
| 1 = BUS LINK NOT IN BYPASS POSITION | EOH2-SDS-D1 | B-4F1005 SH. 632 | B41 | F B | BRN TAN | 9B 9A | 9 |
| 1 = BUS LINK IN BYPASS POSITION | EOH2-SDS-D1 | B-4F1005 SH. 632 | B42 | F B | RED TAN | 10B 10A | 10 |
| 1 = AIR PRESSURE LOW | EOH2-SDS-D1 | B-4F1005 SH. 632 | B43 | F B | ORN TAN | 11B 11A | 11 |
|  |  |  | B44 | F B | YLW TAN | 12B 12A | 12 |
|  |  |  | B45 | F B | GRN TAN | 13B 13A | 13 |
|  |  |  | B46 | F B | BLU TAN | 14B 14A | 14 |
|  |  |  | B47 | F B | VIO TAN | 15B 15A | 15 |
|  |  |  | B48 | F B | GRY TAN | 16B 16A | 16 |

| SLOT NO.: 09 | MODULE TYPE 322 DIGITAL INPUT |
| --- | --- |

| SIGNAL NAME | DEVICE ID | CONT. DWG | CROSS |  | CLR | PIN# | CH |
| --- | --- | --- | --- | --- | --- | --- | --- |
| HF HARDWRE CNTL SYSTEM : 0 = LVL 4X FAULT ALL CB TRIP | EEF1-CBD-EF1-D3 | B-4F1005 SH. 760,761 | B49 | F B | BRN TAN | 1B 1A | 1 |
| 0 = LVL 1 FALT, ALL BKR TRIP | EEF1-CBD-EF1-D3 | B-4F1005 SH. 760,761 | B50 | F B | RED TAN | 2B 2A | 2 |
| 0 = LVL 3 FALT, ALL BKR TRIP | EEF1-CBD-EF1-D3 | B-4F1005 SH. 760,761 | B51 | F B | ORN TAN | 3B 3A | 3 |
| 1 = LVL 4 FALT, ALL BKR TRIP | EEF1-CBD-EF1-D3 | B-4F1005 SH. 760,761 | B52 | F B | YLW TAN | 4B 4A | 4 |
| 0 = POWER SUPPLY PERM NOT READY | EEF1-CBD-EF1-D3 | B-4F1005 SH. 760,761 | B53 | F B | GRN TAN | 5B 5A | 5 |
| 0 = SDS PERM NOT READY | EEF1-CBD-EF1-D3 | B-4F1005 SH. 760,761 | B54 | F B | BLU TAN | 6B 6A | 6 |
| 1 = AUX SYS FAULT (WATER FLOW/TEMP) | EEF1-CBD-EF1-D3 | B-4F1005 SH. 760,761 | B55 | F B | VIO TAN | 7B 7A | 7 |
| 0 = 120 V AUX POWER OFF (L1)(EF1) | EEF1-CBD-EF1-D3 | B-4F1005 SH. 760,761 | B56 | F B | GRY TAN | 8B 8A | 8 |
| 1 = EF/VC POWER SUPPLY ONLY | EEF1-CBD-EF1-D3 | B-4F1005 SH. 760,761 | B57 | F B | BRN TAN | 9B 9A | 9 |
| 1 = EF/VC SDS ONLY | EEF1-CBD-EF1-D3 | B-4F1005 SH. 760,761 | B58 | F B | RED TAN | 10B 10A | 10 |
| 1 = EF/VC LEVEL 1 FAULT (IMPOSED) | EEF1-CBD-EF1-D3 | B-4F1005 SH. 760,761 | B59 | F B | ORN TAN | 11B 11A | 11 |
| 1 = EF/VC LEVEL 3 FAULT (IMPOSED) | EEF1-CBD-EF1-D3 | B-4F1005 SH. 760,761 | B60 | F B | YLW TAN | 12B 12A | 12 |
| 1 = EF/VC BKR TRIP COMMAND | EEF1-CBD-EF1-D3 | B-4F1005 SH. 760,761 | B61 | F B | GRN TAN | 13B 13A | 13 |
| 1 = EF/VC RESET ACHNOWLEDGED | EEF1-CBD-EF1-D3 | B-4F1005 SH. 760,761 | B62 | F B | BLU TAN | 14B 14A | 14 |
|  |  |  | B63 | F B | VIO TAN | 15B 15A | 15 |
|  |  |  | B64 | F B | GRY TAN | 16B 16A | 16 |

| SLOT NO.: 10 | MODULE TYPE 322 DIGITAL INPUT |
| --- | --- |

| SIGNAL NAME | DEVICE ID | CONT. DWG | CROSS |  | CLR | PIN# | CH |
| --- | --- | --- | --- | --- | --- | --- | --- |
| EF/VC HARDWRE CNTL SYSTEM : 1 = LVL 4X FAULT ALL CB TRIP | EEF1-CBD-EF1-D1 | B-4F1005 SH. 748,749 | B65 | F B | BRN TAN | 1B 1A | 1 |
| 0 = LVL 1 FALT, ALL BKR TRIP | EEF1-CBD-EF1-D1 pc_p1_lvl1mon_CALC | B-4F1005 SH. 748,749 | B66 | F B | RED TAN | 2B 2A | 2 |
| 0 = LVL 3 FALT, ALL BKR TRIP | EEF1-CBD-EF1-D1 | B-4F1005 SH. 748,749 | B67 | F B | ORN TAN | 3B 3A | 3 |
| 1 = LVL 4 FALT, ALL BKR TRIP | EEF1-CBD-EF1-D1 | B-4F1005 SH. 748,749 | B68 | F B | YLW TAN | 4B 4A | 4 |
| 0 = POWER SUPPLY PERM NOT READY | EEF1-CBD-EF1-D1 | B-4F1005 SH. 748,749 | B69 | F B | GRN TAN | 5B 5A | 5 |
| 0 = SDS PERM NOT READY | EEF1-CBD-EF1-D1 | B-4F1005 SH. 748,749 | B70 | F B | BLU TAN | 6B 6A | 6 |
| 1 = AUX SYS FAULT (WATER FLOW/TEMP) | EEF1-CBD-EF1-D1 | B-4F1005 SH. 748,749 | B71 | F B | VIO TAN | 7B 7A | 7 |
| 0 = 120 V AUX POWER OFF (L1)(EF1) | EEF1-CBD-EF1-D1 | B-4F1005 SH. 748,749 | B72 | F B | GRY TAN | 8B 8A | 8 |
| 1 = EF/VC POWER SUPPLY ONLY | EEF1-CBD-EF1-D1 | B-4F1005 SH. 748,749 | B73 | F B | BRN TAN | 9B 9A | 9 |
| 1 = EF/VC SDS ONLY | EEF1-CBD-EF1-D1 pc_ef_sdsonly_CALC | B-4F1005 SH. 748,749 | B74 | F B | RED TAN | 10B 10A | 10 |
| 1 = EF/VC LEVEL 1 FAULT (IMPOSED) | EEF1-CBD-EF1-D1 | B-4F1005 SH. 748,749 | B75 | F B | ORN TAN | 11B 11A | 11 |
| 1 = EF/VC LEVEL 3 FAULT (IMPOSED) | EEF1-CBD-EF1-D1 pc_ef_lvl3mon_CALC | B-4F1005 SH. 748,749 | B76 | F B | YLW TAN | 12B 12A | 12 |
| 1 = EF/VC BKR TRIP COMMAND | EEF1-CBD-EF1-D1 | B-4F1005 SH. 748,749 | B77 | F B | GRN TAN | 13B 13A | 13 |
| 1 = EF/VC RESET ACHNOWLEDGED | EEF1-CBD-EF1-D1 | B-4F1005 SH. 748,749 | B78 | F B | BLU TAN | 14B 14A | 14 |
| 1 = RESET ACKNOWLEDGED STATUS FOR VARIOUS SYSTEMS | EEF1-PSS-1C-D7 THRU EEF4-PSS-1C-D7, EEF1-PSS-2C-D7 THRU EEF4-PSS-2C-D7, EFVC-PSS-1C-D7, EHF-PSS-1C-D7 | SEE DC PORTION OF EACH DEVICE | B79 | F B | VIO TAN | 15B 15A | 15 |
|  |  |  | B80 | F B | GRY TAN | 16B 16A | 16 |

| SLOT NO.: 11 | MODULE TYPE 322 DIGITAL INPUT |
| --- | --- |

| SIGNAL NAME | DEVICE ID | CONT. DWG | CROSS |  | CLR | PIN# | CH |
| --- | --- | --- | --- | --- | --- | --- | --- |
| (One TF Branch) 27 Relay Status | R7/RST pc_nstxH27Br1Mon_CALC | B-4F1005 SH. 1602 | D1 | F B | BRN TAN | 1B 1A | 1 |
| (One TF Branch) 27 Relay Status | R3/RST pc_nstxH27Br2Mon_CALC | B-4F1005 SH. 1603 | D2 | F B | RED TAN | 2B 2A | 2 |
| (One TF Branch) 27 Relay Status | R1/RST pc_nstxH27Br3Mon_CALC | B-4F1005 SH. 1604 | D3 | F B | ORN TAN | 3B 3A | 3 |
| (One TF Branch) 27 Relay Status | R2/RST pc_nstxH27Br4Mon_CALC | B-4F1005 SH. 1067 | D4 | F B | YLW TAN | 4B 4A | 4 |
| (23 series devices) 27 Relay Status | R4/RST pc_nstxH27SerMon_CALC | B-4F1005 SH. 1623 | D5 | F B | GRN TAN | 5B 5A | 5 |
| PF4 27 Relay Status | R6/XT pc_nstxH27PF4Mon_CALC | B-4F1005 SH. 1661 | D6 | F B | BLU TAN | 6B 6A | 6 |
| PF2L 27 Relay Status | R5/XT pc_nstxH27PF2LMon_CALC | B-4F1005 SH. 1643 | D7 | F B | VIO TAN | 7B 7A | 7 |
|  |  |  | D8 | F B | GRY TAN | 8B 8A | 8 |
|  |  |  | D9 | F B | BRN TAN | 9B 9A | 9 |
|  |  |  | D10 | F B | RED TAN | 10B 10A | 10 |
|  |  |  | D11 | F B | ORN TAN | 11B 11A | 11 |
|  |  |  | D12 | F B | YLW TAN | 12B 12A | 12 |
|  |  |  | D13 | F B | GRN TAN | 13B 13A | 13 |
|  |  |  | D14 | F B | BLU TAN | 14B 14A | 14 |
|  |  |  | D15 | F B | VIO TAN | 15B 15A | 15 |
|  |  |  | D16 | F B | GRY TAN | 16B 16A | 16 |

| SLOT NO.: 12 | MODULE TYPE 302 DIGITAL OUTPUT |
| --- | --- |

| SIGNAL NAME | DEVICE ID | CONT. DWG | CROSS |  | CLR | PIN# | CH |
| --- | --- | --- | --- | --- | --- | --- | --- |
| SDS CONTRL FOR OH1 CONVERTR: BIT 0 | EOH1-SDS-D1 | B-4F1005 SH. 631 | D17 | F B | BRN TAN | 3B 3A | 1 |
| BIT 1 | EOH1-SDS-D1 | B-4F1005 SH. 631 | D18 | F B | RED TAN | 4B 4A | 2 |
| BIT 2 | EOH1-SDS-D1 | B-4F1005 SH. 631 | D19 | F B | ORN TAN | 5B 5A | 3 |
| BIT 3 | EOH1-SDS-D1 | B-4F1005 SH. 631 | D20 | F B | YLW TAN | 6B 6A | 4 |
| SDS CONTRL FOR OH4 CONVERTR: BIT 0 | EOH4-SDS-D1 | B-4F1005 SH. 672 | D21 | F B | GRN TAN | 7B 7A | 5 |
| BIT 1 | EOH4-SDS-D1 | B-4F1005 SH. 672 | D22 | F B | BLU TAN | 8B 8A | 6 |
| BIT 2 | EOH4-SDS-D1 | B-4F1005 SH. 672 | D23 | F B | VIO TAN | 9B 9A | 7 |
| BIT 3 | EOH4-SDS-D1 | B-4F1005 SH. 672 | D24 | F B | GRY TAN | 10B 10A | 8 |
| SDS CONTRL FOR EF1 CONVERTR: BIT 0 | EEF1-SDS-D1 | B-4F1005 SH. 419 | D25 | F B | BRN TAN | 11B 11A | 9 |
| BIT 1 | EEF1-SDS-D1 | B-4F1005 SH. 419 | D26 | F B | RED TAN | 12B 12A | 10 |
| BIT 2 | EEF1-SDS-D1 | B-4F1005 SH. 419 | D27 | F B | ORN TAN | 13B 13A | 11 |
| BIT 3 | EEF1-SDS-D1 | B-4F1005 SH. 419 | D28 | F B | YLW TAN | 14B 14A | 12 |
| SDS CONTRL FOR EF2 CONVERTR: BIT 0 | EEF2-SDS-D1 | B-4F1005 SH. 454 | D29 | F B | GRN TAN | 15B 15A | 13 |
| BIT 1 | EEF2-SDS-D1 | B-4F1005 SH. 454 | D30 | F B | BLU TAN | 16B 16A | 14 |
| BIT 2 | EEF2-SDS-D1 | B-4F1005 SH. 454 | D31 | F B | VIO TAN | 17B 17A | 15 |
| BIT 3 | EEF2-SDS-D1 | B-4F1005 SH. 454 | D32 | F B | GRY TAN | 18B 18A | 16 |

| SLOT NO.: 13 | MODULE TYPE 302 DIGITAL OUTPUT |
| --- | --- |

| SIGNAL NAME | DEVICE ID | CONT. DWG | CROSS |  | CLR | PIN# | CH |
| --- | --- | --- | --- | --- | --- | --- | --- |
| SDS CONTRL FOR TF2 CONVERTR: BIT 0 | ETF2-SDS-D2 NSTX OHgndCLS | B-4F1005 SH. 1021 | D33 | F B | BRN TAN | 3B 3A | 1 |
| BIT 1 | ETF2-SDS-D2 NSTX OHgndOPN | B-4F1005 SH. 1021 | D34 | F B | RED TAN | 4B 4A | 2 |
| BIT 2 | ETF2-SDS-D2 NSTX OH1lnCLS | B-4F1005 SH. 1021 | D35 | F B | ORN TAN | 5B 5A | 3 |
| BIT 3 | ETF2-SDS-D2 NSTX OH1lnOPN | B-4F1005 SH. 1021 | D36 | F B | YLW TAN | 6B 6A | 4 |
| BIT 4 | ETF2-SDS-D2 NSTX OH2lnCLS | B-4F1005 SH. 1021 | D37 | F B | GRN TAN | 7B 7A | 5 |
| BIT 5 | ETF2-SDS-D2 NSTX OH2lnOPN | B-4F1005 SH. 1021 | D38 | F B | BLU TAN | 8B 8A | 6 |
| BIT 6 | ETF2-SDS-D2 NSTX spare | B-4F1005 SH. 1021 | D39 | F B | VIO TAN | 9B 9A | 7 |
| BIT 7 | ETF2-SDS-D2 NSTX spare | B-4F1005 SH. 1021 | D40 | F B | GRY TAN | 10B 10A | 8 |
| BIT 8 | ETF2-SDS-D2 NSTX RWMlnCLS | B-4F1005 SH. 1021 | D41 | F B | BRN TAN | 11B 11A | 9 |
| BIT 9 | ETF2-SDS-D2 NSTX RWMlnOPN | B-4F1005 SH. 1021 | D42 | F B | RED TAN | 12B 12A | 10 |
| SDS CONTRL FOR OH2 CONVERTR: BIT 0 | EOH2-SDS-D1 | B-4F1005 SH. 632 | D43 | F B | ORN TAN | 13B 13A | 11 |
| BIT 1 | EOH2-SDS-D1 | B-4F1005 SH. 632 | D44 | F B | YLW TAN | 14B 14A | 12 |
| BIT 2 | EOH2-SDS-D1 | B-4F1005 SH. 632 | D45 | F B | GRN TAN | 15B 15A | 13 |
| BIT 3 | EOH2-SDS-D1 | B-4F1005 SH. 632 | D46 | F B | BLU TAN | 16B 16A | 14 |
|  |  |  | D47 | F B | VIO TAN | 17B 17A | 15 |
| VC UV (EF4 CONVERTER) : BIT 0 | EPC-XT-UV1 | B-4F1005 SH. 1087 | D48 | F B | GRY TAN | 18B 18A | 16 |

| SLOT NO.: 14 | MODULE TYPE 302 DIGITAL OUTPUT |
| --- | --- |

| SIGNAL NAME | DEVICE ID | CONT. DWG | CROSS |  | CLR | PIN# | CH |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | D49 | F B | BRN TAN | 3B 3A | 1 |
|  |  |  | D50 | F B | RED TAN | 4B 4A | 2 |
|  |  |  | D51 | F B | ORN TAN | 5B 5A | 3 |
|  |  |  | D52 | F B | YLW TAN | 6B 6A | 4 |
|  |  |  | D53 | F B | GRN TAN | 7B 7A | 5 |
|  |  |  | D54 | F B | BLU TAN | 8B 8A | 6 |
| SDS CONTROL FOR HF CONVERTR: BIT 0 | EHF-SDS-D1 | B-4F1005 SH. 581 | D55 | F B | VIO TAN | 9B 9A | 7 |
| BIT 1 | EHF-SDS-D1 | B-4F1005 SH. 581 | D56 | F B | GRY TAN | 10B 10A | 8 |
| BIT 2 | EHF-SDS-D1 | B-4F1005 SH. 581 | D57 | F B | BRN TAN | 11B 11A | 9 |
| BIT 3 | EHF-SDS-D1 | B-4F1005 SH. 581 | D58 | F B | RED TAN | 12B 12A | 10 |
| SDS CONTROL FOR FOH SHARED COIL: BIT 0 | EFOH-SDS-D1 NSTX RWMgndOPN | B-4F1005 SH. 420 | D59 | F B | ORN TAN | 13B 13A | 11 |
| BIT 1 | EFOH-SDS-D1 NSTX RWMgndCLS | B-4F1005 SH. 420 | D60 | F B | YLW TAN | 14B 14A | 12 |
| BIT 2 | EFOH-SDS-D1 | B-4F1005 SH. 420 | D61 | F B | GRN TAN | 15B 15A | 13 |
| BIT 3 | EFOH-SDS-D1 | B-4F1005 SH. 420 | D62 | F B | BLU TAN | 16B 16A | 14 |
| BIT 4 | EFOH-SDS-D1 | B-4F1005 SH. 420 | D63 | F B | VIO TAN | 17B 17A | 15 |
| BIT 5 | EFOH-SDS-D1 | B-4F1005 SH. 420 | D64 | F B | GRY TAN | 18B 18A | 16 |

| SLOT NO.: 15 | MODULE TYPE 302 DIGITAL OUTPUT |
| --- | --- |

| SIGNAL NAME | DEVICE ID | CONT. DWG | CROSS |  | CLR | PIN# | CH |
| --- | --- | --- | --- | --- | --- | --- | --- |
| GROUND FAULT DET/TEST SYSTEM: BIT 0 | EPC-XT-UV | B-4F1005 SH. 1067 | D65 | F B | BRN TAN | 3B 3A | 1 |
| BIT 1 | EPC-XT-UV | B-4F1005 SH. 1067 | D66 | F B | RED TAN | 4B 4A | 2 |
| BIT 2 | EPC-XT-UV | B-4F1005 SH. 1067 | D67 | F B | ORN TAN | 5B 5A | 3 |
| BIT 3 | EPC-XT-UV | B-4F1005 SH. 1067 | D68 | F B | YLW TAN | 6B 6A | 4 |
| BIT 4 | EPC-XT-UV | B-4F1005 SH. 1067 | D69 | F B | GRN TAN | 7B 7A | 5 |
| BIT 5 | EPC-XT-UV | B-4F1005 SH. 1067 | D70 | F B | BLU TAN | 8B 8A | 6 |
| BIT 6 | EPC-XT-UV | B-4F1005 SH. 1067 | D71 | F B | VIO TAN | 9B 9A | 7 |
| RWM-SDS-36 ON CMD | sds36ONCMD | B-4F1005 SH 1564 | D72 | F B | GRY TAN | 10B 10A | 8 |
| RWM-SDS-36 OFF CMD | sds36OFFCMD | B-4F1005 SH 1564 | D73 | F B | BRN TAN | 11B 11A | 9 |
| RWM-SDS-36 GND CMD | sds36GNDCMD | B-4F1005 SH 1564 | D74 | F B | RED TAN | 12B 12A | 10 |
| RWM-SDS-14 ON CMD | sds14ONCMD | B-4F1005 SH 1564 | D75 | F B | ORN TAN | 13B 13A | 11 |
| RWM-SDS-14 OFF CMD | sds14OFFCMD | B-4F1005 SH 1564 | D76 | F B | YLW TAN | 14B 14A | 12 |
| RWM-SDS-14 GND CMD | sds14GNDCMD | B-4F1005 SH 1564 | D77 | F B | GRN TAN | 15B 15A | 13 |
| RWM-SDS-25 ON CMD | sds25ONCMD | B-4F1005 SH 1564 | D78 | F B | BLU TAN | 16B 16A | 14 |
| RWM-SDS-25 OFF CMD | sds25OFFCMD | B-4F1005 SH 1564 | D79 | F B | VIO TAN | 17B 17A | 15 |
| RWM-SDS-25 GND CMD | sds25GNDCMD | B-4F1005 SH 1564 | D80 | F B | GRY TAN | 18B 18A | 16 |

| SLOT NO.: 16 | MODULE TYPE 322 DIGITAL INPUT |
| --- | --- |

| SIGNAL NAME | DEVICE ID | CONT. DWG | CROSS |  | CLR | PIN# | CH |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | C1 | F B | BRN TAN | 1B 1A | 1 |
|  |  |  | C2 | F B | RED TAN | 2B 2A | 2 |
|  |  |  | C3 | F B | ORN TAN | 3B 3A | 3 |
|  |  |  | C4 | F B | YLW TAN | 4B 4A | 4 |
|  |  |  | C5 | F B | GRN TAN | 5B 5A | 5 |
|  |  |  | C6 | F B | BLU TAN | 6B 6A | 6 |
|  |  |  | C7 | F B | VIO TAN | 7B 7A | 7 |
|  |  |  | C8 | F B | GRY TAN | 8B 8A | 8 |
|  |  |  | C9 | F B | BRN TAN | 9B 9A | 9 |
|  |  |  | C10 | F B | RED TAN | 10B 10A | 10 |
|  |  |  | C11 | F B | ORN TAN | 11B 11A | 11 |
|  |  |  | C12 | F B | YLW TAN | 12B 12A | 12 |
|  |  |  | C13 | F B | GRN TAN | 13B 13A | 13 |
|  |  |  | C14 | F B | BLU TAN | 14B 14A | 14 |
|  |  |  | C15 | F B | VIO TAN | 15B 15A | 15 |
|  |  |  | C16 | F B | GRY TAN | 16B 16A | 16 |

| SLOT NO.: 17 | MODULE TYPE 322 DIGITAL INPUT |
| --- | --- |

| SIGNAL NAME | DEVICE ID | CONT. DWG | CROSS |  | CLR | PIN# | CH |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | C17 | F B | BRN TAN | 1B 1A | 1 |
|  |  |  | C18 | F B | RED TAN | 2B 2A | 2 |
|  |  |  | C19 | F B | ORN TAN | 3B 3A | 3 |
|  |  |  | C20 | F B | YLW TAN | 4B 4A | 4 |
|  |  |  | C21 | F B | GRN TAN | 5B 5A | 5 |
|  |  |  | C22 | F B | BLU TAN | 6B 6A | 6 |
|  |  |  | C23 | F B | VIO TAN | 7B 7A | 7 |
|  |  |  | C24 | F B | GRY TAN | 8B 8A | 8 |
|  |  |  | C25 | F B | BRN TAN | 9B 9A | 9 |
|  |  |  | C26 | F B | RED TAN | 10B 10A | 10 |
|  |  |  | C27 | F B | ORN TAN | 11B 11A | 11 |
|  |  |  | C28 | F B | YLW TAN | 12B 12A | 12 |
|  |  |  | C29 | F B | GRN TAN | 13B 13A | 13 |
|  |  |  | C30 | F B | BLU TAN | 14B 14A | 14 |
|  |  |  | C31 | F B | VIO TAN | 15B 15A | 15 |
|  |  |  | C32 | F B | GRY TAN | 16B 16A | 16 |

| SLOT NO.: 18 | MODULE TYPE 322 DIGITAL INPUT |
| --- | --- |

| SIGNAL NAME | DEVICE ID | CONT. DWG | CROSS |  | CLR | PIN# | CH |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | C33 | F B | BRN TAN | 1B 1A | 1 |
|  |  |  | C34 | F B | RED TAN | 2B 2A | 2 |
|  |  |  | C35 | F B | ORN TAN | 3B 3A | 3 |
|  |  |  | C36 | F B | YLW TAN | 4B 4A | 4 |
|  |  |  | C37 | F B | GRN TAN | 5B 5A | 5 |
|  |  |  | C38 | F B | BLU TAN | 6B 6A | 6 |
|  |  |  | C39 | F B | VIO TAN | 7B 7A | 7 |
|  |  |  | C40 | F B | GRY TAN | 8B 8A | 8 |
|  |  |  | C41 | F B | BRN TAN | 9B 9A | 9 |
|  |  |  | C42 | F B | RED TAN | 10B 10A | 10 |
|  |  |  | C43 | F B | ORN TAN | 11B 11A | 11 |
|  |  |  | C44 | F B | YLW TAN | 12B 12A | 12 |
|  |  |  | C45 | F B | GRN TAN | 13B 13A | 13 |
|  |  |  | C46 | F B | BLU TAN | 14B 14A | 14 |
|  |  |  | C47 | F B | VIO TAN | 15B 15A | 15 |
|  |  |  | C48 | F B | GRY TAN | 16B 16A | 16 |

| SLOT NO.: 19 | MODULE TYPE 322 DIGITAL INPUT |
| --- | --- |

| SIGNAL NAME | DEVICE ID | CONT. DWG | CROSS |  | CLR | PIN# | CH |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | C49 | F B | BRN TAN | 1B 1A | 1 |
|  |  |  | C50 | F B | RED TAN | 2B 2A | 2 |
|  |  |  | C51 | F B | ORN TAN | 3B 3A | 3 |
|  |  |  | C52 | F B | YLW TAN | 4B 4A | 4 |
|  |  |  | C53 | F B | GRN TAN | 5B 5A | 5 |
|  |  |  | C54 | F B | BLU TAN | 6B 6A | 6 |
|  |  |  | C55 | F B | VIO TAN | 7B 7A | 7 |
|  |  |  | C56 | F B | GRY TAN | 8B 8A | 8 |
|  |  |  | C57 | F B | BRN TAN | 9B 9A | 9 |
|  |  |  | C58 | F B | RED TAN | 10B 10A | 10 |
|  |  |  | C59 | F B | ORN TAN | 11B 11A | 11 |
|  |  |  | C60 | F B | YLW TAN | 12B 12A | 12 |
|  |  |  | C61 | F B | GRN TAN | 13B 13A | 13 |
|  |  |  | C62 | F B | BLU TAN | 14B 14A | 14 |
|  |  |  | C63 | F B | VIO TAN | 15B 15A | 15 |
|  |  |  | C64 | F B | GRY TAN | 16B 16A | 16 |

| SLOT NO.: 21 | MODULE TYPE 322 DIGITAL INPUT |
| --- | --- |

| SIGNAL NAME | DEVICE ID | CONT. DWG | CROSS |  | CLR | PIN# | CH |
| --- | --- | --- | --- | --- | --- | --- | --- |
| (One TF Branch) Halmar 27 Relay Reset | R7/RST | B-4F1005 SH. 1602 | E1 | F B | BRN TAN | 1B 1A | 1 |
| (One TF Branch) Halmar 27 Relay Reset | R3/RST | B-4F1005 SH. 1603 | E2 | F B | RED TAN | 2B 2A | 2 |
| (One TF Branch) Halmar 27 Relay Reset | R1/RST | B-4F1005 SH. 1604 | E3 | F B | ORN TAN | 3B 3A | 3 |
| (One TF Branch) Halmar 27 Relay Reset | R2/RST | B-4F1005 SH. 1605 | E4 | F B | YLW TAN | 4B 4A | 4 |
| (23 series devices) Halmar 27 Relay Reset | R4/RST | B-4F1005 SH. 1623 | E5 | F B | GRN TAN | 5B 5A | 5 |
| PF4, Halmar 27 Relay Reset | R6/RST | B-4F1005 SH. 1661 | E6 | F B | BLU TAN | 6B 6A | 6 |
| PF2l, Halmar 27 Relay Reset | R5/RST | B-4F1005 SH. 1643 | E7 | F B | VIO TAN | 7B 7A | 7 |
| BIT 7 | EEF-PSS-SYS-D1 | B-4F1005 SH. 593 | E8 | F B | GRY TAN | 8B 8A | 8 |
| BIT 8 | EEF-PSS-SYS-D1 | B-4F1005 SH. 593 | E9 | F B | BRN TAN | 9B 9A | 9 |
| BIT 9 | EEF-PSS-SYS-D1 | B-4F1005 SH. 593 | E10 | F B | RED TAN | 10B 10A | 10 |
| BIT 10 | EEF-PSS-SYS-D1 | B-4F1005 SH. 593 | E11 | F B | ORN TAN | 11B 11A | 11 |
| BIT 11 | EEF-PSS-SYS-D1 | B-4F1005 SH. 593 | E12 | F B | YLW TAN | 12B 12A | 12 |
| BIT 12 | EEF-PSS-SYS-D1 | B-4F1005 SH. 593 | E13 | F B | GRN TAN | 13B 13A | 13 |
| BIT 13 | EEF-PSS-SYS-D1 | B-4F1005 SH. 593 | E14 | F B | BLU TAN | 14B 14A | 14 |
| BIT 14 | EEF-PSS-SYS-D1 | B-4F1005 SH. 593 | E15 | F B | VIO TAN | 15B 15A | 15 |
| BIT 15 | EEF-PSS-SYS-D1 | B-4F1005 SH. 593 | E16 | F B | GRY TAN | 16B 16A | 16 |

| SLOT NO.: 22 | MODULE TYPE 322 DIGITAL INPUT |
| --- | --- |

| SIGNAL NAME | DEVICE ID | CONT. DWG | CROSS |  | CLR | PIN# | CH |
| --- | --- | --- | --- | --- | --- | --- | --- |
| EF SYSTEM : BIT 0 | EEF-PSS-SYS-D2 | B-4F1005 SH. 592,586 | E17 | F B | BRN TAN | 1B 1A | 1 |
| BIT 1 | EEF-PSS-SYS-D2 | B-4F1005 SH. 592,586 | E18 | F B | RED TAN | 2B 2A | 2 |
| BIT 2 | EEF-PSS-SYS-D2 | B-4F1005 SH. 592,586 | E19 | F B | ORN TAN | 3B 3A | 3 |
| BIT 3 | EEF-PSS-SYS-D2 | B-4F1005 SH. 592,586 | E20 | F B | YLW TAN | 4B 4A | 4 |
| BIT 4 | EEF-PSS-SYS-D2 | B-4F1005 SH. 592,586 | E21 | F B | GRN TAN | 5B 5A | 5 |
| BIT 5 | EEF-PSS-SYS-D2 | B-4F1005 SH. 592,586 | E22 | F B | BLU TAN | 6B 6A | 6 |
| BIT 6 | EEF-PSS-SYS-D2 | B-4F1005 SH. 592,586 | E23 | F B | VIO TAN | 7B 7A | 7 |
| BIT 7 | EEF-PSS-SYS-D2 | B-4F1005 SH. 592,586 | E24 | F B | GRY TAN | 8B 8A | 8 |
|  |  |  | E25 | F B | BRN TAN | 9B 9A | 9 |
|  |  |  | E26 | F B | RED TAN | 10B 10A | 10 |
|  |  |  | E27 | F B | ORN TAN | 11B 11A | 11 |
|  |  |  | E28 | F B | YLW TAN | 12B 12A | 12 |
|  |  |  | E29 | F B | GRN TAN | 13B 13A | 13 |
|  |  |  | E30 | F B | BLU TAN | 14B 14A | 14 |
|  |  |  | E31 | F B | VIO TAN | 15B 15A | 15 |
|  |  |  | E32 | F B | GRY TAN | 16B 16A | 16 |

# Text boxes

NSTX

NSTX

NSTX

NSTX

NSTX

NSTX

NSTX

NSTX

NSTX

NSTX

NSTX

| RWM-SDS-14 ON CMD | sds14ONCMD | B-4F1005 SH 1564 |
| --- | --- | --- |
| RWM-SDS-14 OFF CMD | sds14OFFCMD | B-4F1005 SH 1564 |
| RWM-SDS-14 GND CMD | sds14GNDCMD | B-4F1005 SH 1564 |

NSTX

| RWM-SDS-14 ON CMD | sds14ONCMD | B-4F1005 SH 1564 |
| --- | --- | --- |
| RWM-SDS-14 OFF CMD | sds14OFFCMD | B-4F1005 SH 1564 |
| RWM-SDS-14 GND CMD | sds14GNDCMD | B-4F1005 SH 1564 |

NSTX

NSTX

NSTX