| CRATE LAYOUT DESCRIPTION |  |
| --- | --- |

| SLOT | CROSS-CX | MODULE DESCRIPTION & STRAPPING |
| --- | --- | --- |
| NSTX 1 | A01 - A16 | 322 16-BIT DIGITAL INPUT MODULE - ISOLATED CONTACT |
| NSTX 2 | A17 - A32 | 322 16-BIT DIGITAL INPUT MODULE - ISOLATED CONTACT |
| NSTX 3 | A33 - A48 | 322 16-BIT DIGITAL INPUT MODULE - ISOLATED CONTACT |
| NSTX 4 | A49 - A64 | 322 16-BIT DIGITAL INPUT MODULE - ISOLATED CONTACT |
| NSTX 5 | A65 - A80 | 322 16-BIT DIGITAL INPUT MODULE - ISOLATED CONTACT |
| NSTX 6 | B01 - B16 | 322 16-BIT DIGITAL INPUT MODULE - ISOLATED CONTACT |
| NSTX 7 | B17 - B32 | 322 16-BIT DIGITAL INPUT MODULE - ISOLATED CONTACT |
| NSTX 8 | B33 - B48 | 16-BIT DIGITAL OUTPUT MODULE - 302 RELAY OUTPUTS, MOMENTARY, NORM OPEN |
| NSTX 9 | B49 - B64 | 16-BIT DIGITAL OUTPUT MODULE - 302 RELAY OUTPUTS, MOMENTARY, NORM OPEN |
| NSTX 10 | B65 - B80 | 320 16 CHANNEL SCANNING ADC [+/- 10 V] |
| NSTX 11 | D01 - D16 | 16-BIT DIGITAL OUTPUT MODULE - 302 RELAY OUTPUTS, MOMENTARY, NORM OPEN |
| NSTX 12 | D17 - D32 | 16-BIT DIGITAL OUTPUT MODULE - 302 RELAY OUTPUTS, MOMENTARY, NORM OPEN |
| 13 | D33 - D48 | 322 16-BIT DIGITAL INPUT MODULE - ISOLATED CONTACT |
| NSTX 14 | D49 - D64 | 322 16-BIT DIGITAL INPUT MODULE - ISOLATED CONTACT |
| 15 | ---- | 903 32 KW MEMORY MODULE [00000] |
| NSTX 16 | D65 - D80 | 908 32 CHANNEL TRANSIENT DIGITIZER [+/- 5 V , 32 KW, P2 CLK] |
| 17 | ---- | 908 (SLOT 2 OF 3) |
| 18 | (T1) | 908 (SLOT 3 OF 3) |
| NSTX 19 | C01 - C16 | 322 16 BIT DIGITAL INPUT MODULE - ISOLATED CONTACT |
| 20 | ---- | 404A 8 CHANNEL TIMING MODULE [E-STOP OFF] |
| 21 | (T1) | 404A (SLOT 2 OF 2) |
| 22 | ---- | --- PC LINK REPEATER/RESTORER MODULE |
| 23 | ---- | 313 U-PORT ADAPTER (& FACILITY CLOCK) |
| 24/25 | ---- | 3952 L-2 CRATE CONTROLLER |

| SLOT NO.: 01 | MODULE TYPE 322 DIGITAL INPUT |
| --- | --- |

| SIGNAL NAME | DEVICE ID | CONT. DWG | CROSS |  | CLR | PIN# | CH |
| --- | --- | --- | --- | --- | --- | --- | --- |
| SDS STATS FOR FVC CONVERTER: 1 = CONTROL READY | EFVC-SDS-D1 | B-4F1005 SH. 490 | A1 | F B | BRN TAN | 1B 1A | 1 |
| 1 = DOORS CLOSED | EFVC-SDS-D1 | B-4F1005 SH. 490 | A2 | F B | RED TAN | 2B 2A | 2 |
| 1 = GROUNDING SWITCH CLOSED | EFVC-SDS-D1 | B-4F1005 SH. 490 | A3 | F B | ORN TAN | 3B 3A | 3 |
| 1 = GROUNDING SWITCH OPEN | EFVC-SDS-D1 | B-4F1005 SH. 490 | A4 | F B | YLW TAN | 4B 4A | 4 |
| 1 = LINE SWITCH CLOSED | EFVC-SDS-D1 | B-4F1005 SH. 490 | A5 | F B | GRN TAN | 5B 5A | 5 |
| 1 = LINE SWITCH OPEN | EFVC-SDS-D1 | B-4F1005 SH. 490 | A6 | F B | BLU TAN | 6B 6A | 6 |
| 0 = BUS LINK NOT NORMAL | EFVC-SDS-D1 | B-4F1005 SH. 490 | A7 | F B | VIO TAN | 7B 7A | 7 |
| 1 = BUS LINK REVERSED | EFVC-SDS-D1 | B-4F1005 SH. 490 | A8 | F B | GRY TAN | 8B 8A | 8 |
| 1 = BUS LINK NOT IN BYPASS POSITION | EFVC-SDS-D1 | B-4F1005 SH. 490 | A9 | F B | BRN TAN | 9B 9A | 9 |
| 1 = BUS LINK IN BYPASS POSITION | EFVC-SDS-D1 | B-4F1005 SH. 490 | A10 | F B | RED TAN | 10B 10A | 10 |
| 1 = AIR PRESSURE LOW | EFVC-SDS-D1 | B-4F1005 SH. 490 | A11 | F B | ORN TAN | 11B 11A | 11 |
| TF GROUND FAULT BIT 0 | ETF-GFD-MON |  | A12 | F B | YLW TAN | 12B 12A | 12 |
| BIT 1 | ETF-GFD-MON |  | A13 | F B | GRN TAN | 13B 13A | 13 |
| SDS STATS FOR TF1 CONVERTER: 1 = AIR PRESSURE LOW | ETF1-SDS-D1 | B-4F1005 SH. 891 | A14 | F B | BLU TAN | 14B 14A | 14 |
| 1 = CONTROL READY | ETF1-SDS-D1 | B-4F1005 SH. 891 | A15 | F B | VIO TAN | 15B 15A | 15 |
|  |  |  | A16 | F B | GRY TAN | 16B 16A | 16 |

| SLOT NO.: 02 | MODULE TYPE 322 DIGITAL INPUT |
| --- | --- |

| SIGNAL NAME | DEVICE ID | CONT. DWG | CROSS |  | CLR | PIN# | CH |
| --- | --- | --- | --- | --- | --- | --- | --- |
| SDS STATS FOR TF1 CONVERTER: 1 = DOORS CLOSED | ETF1-SDS-D2 | B-4F1005 SH. 801 | A17 | F B | BRN TAN | 1B 1A | 1 |
| 1 = GROUNDING SWITCH CLOSED | ETF1-SDS-D2 | B-4F1005 SH. 801 | A18 | F B | RED TAN | 2B 2A | 2 |
| 1 = GROUNDING SWITCH OPEN | ETF1-SDS-D2 | B-4F1005 SH. 801 | A19 | F B | ORN TAN | 3B 3A | 3 |
| 1 = LINE SWITCH 1 CLOSED | ETF1-SDS-D2 | B-4F1005 SH. 801 | A20 | F B | YLW TAN | 4B 4A | 4 |
| 1 = LINE SWITCH 1 OPEN | ETF1-SDS-D2 | B-4F1005 SH. 801 | A21 | F B | GRN TAN | 5B 5A | 5 |
| 1 = LINE SWITCH 2 CLOSED | ETF1-SDS-D2 | B-4F1005 SH. 801 | A22 | F B | BLU TAN | 6B 6A | 6 |
| 1 = LINE SWITCH 2 OPEN | ETF1-SDS-D2 | B-4F1005 SH. 801 | A23 | F B | VIO TAN | 7B 7A | 7 |
| 1 = LINE SWITCH 3 CLOSED | ETF1-SDS-D2 | B-4F1005 SH. 801 | A24 | F B | GRY TAN | 8B 8A | 8 |
| 1 = LINE SWITCH 3 OPEN | ETF1-SDS-D2 | B-4F1005 SH. 801 | A25 | F B | BRN TAN | 9B 9A | 9 |
| 1 = LINE SWITCH 4 CLOSED | ETF1-SDS-D2 | B-4F1005 SH. 801 | A26 | F B | RED TAN | 10B 10A | 10 |
| 1 = LINE SWITCH 4 OPEN | ETF1-SDS-D2 | B-4F1005 SH. 801 | A27 | F B | ORN TAN | 11B 11A | 11 |
| 0 = BRANCH 1 BUS LINK NOT NORMAL | ETF1-SDS-D2 | B-4F1005 SH. 801 | A28 | F B | YLW TAN | 12B 12A | 12 |
| 1 = BRANCH 1 BUS LINK REVERSED | ETF1-SDS-D2 | B-4F1005 SH. 801 | A29 | F B | GRN TAN | 13B 13A | 13 |
| 0 = BRANCH 2 BUS LINK NOT NORMAL | ETF1-SDS-D2 | B-4F1005 SH. 801 | A30 | F B | BLU TAN | 14B 14A | 14 |
| 1 = BRANCH 2 BUS LINK REVERSED | ETF1-SDS-D2 | B-4F1005 SH. 801 | A31 | F B | VIO TAN | 15B 15A | 15 |
| SDS STATS FOR TF1 CONVERTER: 1 = CONTROL POWER ON | ETF1-CBD-TF1 | B-4F1005 SH. 900 | A32 | F B | GRY TAN | 16B 16A | 16 |

| SLOT NO.: 03 | MODULE TYPE 322 DIGITAL INPUT |
| --- | --- |

| SIGNAL NAME | DEVICE ID | CONT. DWG | CROSS |  | CLR | PIN# | CH |
| --- | --- | --- | --- | --- | --- | --- | --- |
| TF1 SDS STATUS : 0 = BRANCH 3 BUS LINK NOT NORMAL | ETF1-SDS-D3 | B-4F1005 SH. 891 | A33 | F B | BRN TAN | 1B 1A | 1 |
| 1 = BRANCH 3 BUS LINK REVERSED | ETF1-SDS-D3 | B-4F1005 SH. 891 | A34 | F B | RED TAN | 2B 2A | 2 |
| 0 = BRANCH 4 BUS LINK NOT NORMAL | ETF1-SDS-D3 | B-4F1005 SH. 891 | A35 | F B | ORN TAN | 3B 3A | 3 |
| 1 = BRANCH 4 BUS LINK REVERSED | ETF1-SDS-D3 | B-4F1005 SH. 891 | A36 | F B | YLW TAN | 4B 4A | 4 |
|  |  |  | A37 | F B | GRN TAN | 5B 5A | 5 |
| SDS STATS FOR FVC CONVERTER: 1 = CONTROL READY | EOH6-SDS-D1 | B-4F1005 SH. 712 | A38 | F B | BLU TAN | 6B 6A | 6 |
| 1 = DOORS CLOSED | EOH6-SDS-D1 | B-4F1005 SH. 712 | A39 | F B | VIO TAN | 7B 7A | 7 |
| 1 = GROUNDING SWITCH CLOSED | EOH6-SDS-D1 | B-4F1005 SH. 712 | A40 | F B | GRY TAN | 8B 8A | 8 |
| 1 = GROUNDING SWITCH OPEN | EOH6-SDS-D1 | B-4F1005 SH. 712 | A41 | F B | BRN TAN | 9B 9A | 9 |
| 1 = LINE SWITCH CLOSED | EOH6-SDS-D1 | B-4F1005 SH. 712 | A42 | F B | RED TAN | 10B 10A | 10 |
| 1 = LINE SWITCH OPEN | EOH6-SDS-D1 | B-4F1005 SH. 712 | A43 | F B | ORN TAN | 11B 11A | 11 |
| 0 = BUS LINK NOT NORMAL | EOH6-SDS-D1 | B-4F1005 SH. 712 | A44 | F B | YLW TAN | 12B 12A | 12 |
| 1 = BUS LINK REVERSED | EOH6-SDS-D1 | B-4F1005 SH. 712 | A45 | F B | GRN TAN | 13B 13A | 13 |
| 1 = BUS LINK NOT IN BYPASS POSITION | EOH6-SDS-D1 | B-4F1005 SH. 712 | A46 | F B | BLU TAN | 14B 14A | 14 |
| 1 = BUS LINK IN BYPASS POSITION | EOH6-SDS-D1 | B-4F1005 SH. 712 | A47 | F B | VIO TAN | 15B 15A | 15 |
| 1 = AIR PRESSURE LOW | EOH6-SDS-D1 | B-4F1005 SH. 712 | A48 | F B | GRY TAN | 16B 16A | 16 |

| SLOT NO.: 04 | MODULE TYPE 322 DIGITAL INPUT |
| --- | --- |

| SIGNAL NAME | DEVICE ID | CONT. DWG | CROSS |  | CLR | PIN# | CH |
| --- | --- | --- | --- | --- | --- | --- | --- |
| SDS STAT FOR EF3 CONVERTR: 1 = CONTROL READY | EEF3-SDS-D1 | B-4F1005 SH. 489 | A49 | F B | BRN TAN | 1B 1A | 1 |
| 1 = DOORS CLOSED | EEF3-SDS-D1 | B-4F1005 SH. 489 | A50 | F B | RED TAN | 2B 2A | 2 |
| 1 = GROUNDING SWITCH CLOSED | EEF3-SDS-D1 | B-4F1005 SH. 489 | A51 | F B | ORN TAN | 3B 3A | 3 |
| 1 = GROUNDING SWITCH OPEN | EEF3-SDS-D1 | B-4F1005 SH. 489 | A52 | F B | YLW TAN | 4B 4A | 4 |
| 1 = LINE SWITCH CLOSED | EEF3-SDS-D1 | B-4F1005 SH. 489 | A53 | F B | GRN TAN | 5B 5A | 5 |
| 1 = LINE SWITCH OPEN | EEF3-SDS-D1 | B-4F1005 SH. 489 | A54 | F B | BLU TAN | 6B 6A | 6 |
| D1 :0 = BUS LINK NOT NORMAL D19 : 1 = 125 VDC OK | EEF3-SDS-D1 & EFDS-D19 | B-4F1005 SH. 489 | A55 | F B | VIO TAN | 7B 7A | 7 |
| 1 = BUS LINK REVERSED | EEF3-SDS-D1 | B-4F1005 SH. 489 | A56 | F B | GRY TAN | 8B 8A | 8 |
| 1 = BUS LINK NOT IN BYPASS POSITION | EEF3-SDS-D1 | B-4F1005 SH. 489 | A57 | F B | BRN TAN | 9B 9A | 9 |
| 1 = BUS LINK IN BYPASS POSITION | EEF3-SDS-D1 | B-4F1005 SH. 489 | A58 | F B | RED TAN | 10B 10A | 10 |
| 1 = AIR PRESSURE LOW | EEF3-SDS-D1 | B-4F1005 SH. 489 | A59 | F B | ORN TAN | 11B 11A | 11 |
| EFDS : HI POT CONTROL OUT: SCALE FACTOR BIT 0 | EFDS-D3 | B-4F1005 SH. 1065,1066 | A60 | F B | YLW TAN | 12B 12A | 12 |
| SCALE FACTOR BIT 1 | EFDS-D3 | B-4F1005 SH. 1065,1066 | A61 | F B | GRN TAN | 13B 13A | 13 |
| 1 = AUTO RAISE/LWR MODE | EFDS-D3 | B-4F1005 SH. 1065,1066 | A62 | F B | BLU TAN | 14B 14A | 14 |
| 1 = MANUAL RAISE/LWR MODE | EFDS-D3 | B-4F1005 SH. 1065,1066 | A63 | F B | VIO TAN | 15B 15A | 15 |
| 1 = INPUT POWER READY | EFDS-D3 | B-4F1005 SH. 1065,1066 | A64 | F B | GRY TAN | 16B 16A | 16 |

| SLOT NO.: 05 | MODULE TYPE 322 DIGITAL INPUT |
| --- | --- |

| SIGNAL NAME | DEVICE ID | CONT. DWG | CROSS |  | CLR | PIN# | CH |
| --- | --- | --- | --- | --- | --- | --- | --- |
| SDS STAT FOR EF4 CONVERTR: 1 = CONTROL READY | EEF4-SDS-D1 | B-4F1005 SH. 524 | A65 | F B | BRN TAN | 1B 1A | 1 |
| 1 = DOORS CLOSED | EEF4-SDS-D1 | B-4F1005 SH. 524 | A66 | F B | RED TAN | 2B 2A | 2 |
| 1 = GROUNDING SWITCH CLOSED | EEF4-SDS-D1 | B-4F1005 SH. 524 | A67 | F B | ORN TAN | 3B 3A | 3 |
| 1 = GROUNDING SWITCH OPEN | EEF4-SDS-D1 | B-4F1005 SH. 524 | A68 | F B | YLW TAN | 4B 4A | 4 |
| 1 = LINE SWITCH CLOSED | EEF4-SDS-D1 | B-4F1005 SH. 524 | A69 | F B | GRN TAN | 5B 5A | 5 |
| 1 = LINE SWITCH OPEN | EEF4-SDS-D1 | B-4F1005 SH. 524 | A70 | F B | BLU TAN | 6B 6A | 6 |
| 0 = BUS LINK NOT NORMAL | EEF4-SDS-D1 | B-4F1005 SH. 524 | A71 | F B | VIO TAN | 7B 7A | 7 |
| 1 = BUS LINK REVERSED | EEF4-SDS-D1 | B-4F1005 SH. 524 | A72 | F B | GRY TAN | 8B 8A | 8 |
| 1 = BUS LINK NOT IN BYPASS POSITION | EEF4-SDS-D1 | B-4F1005 SH. 524 | A73 | F B | BRN TAN | 9B 9A | 9 |
| 1 = BUS LINK IN BYPASS POSITION | EEF4-SDS-D1 | B-4F1005 SH. 524 | A74 | F B | RED TAN | 10B 10A | 10 |
| 1 = AIR PRESSURE LOW | EEF4-SDS-D1 | B-4F1005 SH. 524 | A75 | F B | ORN TAN | 11B 11A | 11 |
| EFDS: GRND Fault 1 = EF Positive Gnd Trip | EFDS-D8 pc_nstxPF3U_pgtrp_DI | B-4F1005 SH. 1068 | A76 | F B | YLW TAN | 12B 12A | 12 |
| 1 = EF Negative Gnd Trip | EFDS-D8 pc_nstxPF3U_ngtrp_DI | B-4F1005 SH. 1068 | A77 | F B | GRN TAN | 13B 13A | 13 |
| 1 = OH Positive Gnd Trip | EFDS-D8 pc_nstxPF2L_pgtrp_DI | B-4F1005 SH. 1068 | A78 | F B | BLU TAN | 14B 14A | 14 |
| 1 = OH Negative Gnd Trip | EFDS-D8 pc_nstxPF2L_ngtrp_DI | B-4F1005 SH. 1068 | A79 | F B | VIO TAN | 15B 15A | 15 |
|  |  |  | A80 | F B | GRY TAN | 16B 16A | 16 |

| SLOT NO.: 06 | MODULE TYPE 322 DIGITAL INPUT |
| --- | --- |

| SIGNAL NAME | DEVICE ID | CONT. DWG | CROSS |  | CLR | PIN# | CH |
| --- | --- | --- | --- | --- | --- | --- | --- |
| SDS STAT FOR OH3 CONVERTR: 1 = CONTROL READY | EOH3-SDS-D1 | B-4F1005 SH. 671 | B1 | F B | BRN TAN | 1B 1A | 1 |
| 1 = DOORS CLOSED | EOH3-SDS-D1 | B-4F1005 SH. 671 | B2 | F B | RED TAN | 2B 2A | 2 |
| 1 = GROUNDING SWITCH CLOSED | EOH3-SDS-D1 | B-4F1005 SH. 671 | B3 | F B | ORN TAN | 3B 3A | 3 |
| 1 = GROUNDING SWITCH OPEN | EOH3-SDS-D1 | B-4F1005 SH. 671 | B4 | F B | YLW TAN | 4B 4A | 4 |
| 1 = LINE SWITCH CLOSED | EOH3-SDS-D1 | B-4F1005 SH. 671 | B5 | F B | GRN TAN | 5B 5A | 5 |
| 1 = LINE SWITCH OPEN | EOH3-SDS-D1 | B-4F1005 SH. 671 | B6 | F B | BLU TAN | 6B 6A | 6 |
| 0 = BUS LINK NOT NORMAL | EOH3-SDS-D1 | B-4F1005 SH. 671 | B7 | F B | VIO TAN | 7B 7A | 7 |
| 1 = BUS LINK REVERSED | EOH3-SDS-D1 | B-4F1005 SH. 671 | B8 | F B | GRY TAN | 8B 8A | 8 |
| 1 = BUS LINK NOT IN BYPASS POSITION | EOH3-SDS-D1 | B-4F1005 SH. 671 | B9 | F B | BRN TAN | 9B 9A | 9 |
| 1 = BUS LINK IN BYPASS POSITION | EOH3-SDS-D1 | B-4F1005 SH. 671 | B10 | F B | RED TAN | 10B 10A | 10 |
| 1 = AIR PRESSURE LOW | EOH3-SDS-D1 | B-4F1005 SH. 671 | B11 | F B | ORN TAN | 11B 11A | 11 |
| EFDS: GRND Fault 1 = TF Positive Gnd Trip | EFDS-D7 pc_nstxTF_pgtrp_DI | B-4F1005 SH. 1068 | B12 | F B | YLW TAN | 12B 12A | 12 |
| 1 = TF Negative Gnd Trip | EFDS-D7 pc_nstxTF_ngtrp_DI | B-4F1005 SH. 1068 | B13 | F B | GRN TAN | 13B 13A | 13 |
| 1 = HF Positive Gnd Trip | EFDS-D7 pc_nstxOH_pgtrp_DI | B-4F1005 SH. 1068 | B14 | F B | BLU TAN | 14B 14A | 14 |
| 1 = HF Negative Gnd Trip | EFDS-D7 pc_nstxOH_ngtrp_DI | B-4F1005 SH. 1068 | B15 | F B | VIO TAN | 15B 15A | 15 |
| 1 = HI POT TRIPPED | EFDS-D7 | B-4F1005 SH. 1068 | B16 | F B | GRY TAN | 16B 16A | 16 |

| SLOT NO.: 07 | MODULE TYPE 322 DIGITAL INPUT |
| --- | --- |

| SIGNAL NAME | DEVICE ID | CONT. DWG | CROSS |  | CLR | PIN# | CH |
| --- | --- | --- | --- | --- | --- | --- | --- |
| SDS STAT FOR OH5 CONVERTR: 1 = CONTROL READY | EOH5-SDS-D1 | B-4F1005 SH. 711 | B17 | F B | BRN TAN | 1B 1A | 1 |
| 1 = DOORS CLOSED | EOH5-SDS-D1 | B-4F1005 SH. 711 | B18 | F B | RED TAN | 2B 2A | 2 |
| 1 = GROUNDING SWITCH CLOSED | EOH5-SDS-D1 | B-4F1005 SH. 711 | B19 | F B | ORN TAN | 3B 3A | 3 |
| 1 = GROUNDING SWITCH OPEN | EOH5-SDS-D1 | B-4F1005 SH. 711 | B20 | F B | YLW TAN | 4B 4A | 4 |
| 1 = LINE SWITCH CLOSED | EOH5-SDS-D1 | B-4F1005 SH. 711 | B21 | F B | GRN TAN | 5B 5A | 5 |
| 1 = LINE SWITCH OPEN | EOH5-SDS-D1 | B-4F1005 SH. 711 | B22 | F B | BLU TAN | 6B 6A | 6 |
| 0 = BUS LINK NOT NORMAL | EOH5-SDS-D1 | B-4F1005 SH. 711 | B23 | F B | VIO TAN | 7B 7A | 7 |
| 1 = BUS LINK REVERSED | EOH5-SDS-D1 | B-4F1005 SH. 711 | B24 | F B | GRY TAN | 8B 8A | 8 |
| 1 = BUS LINK NOT IN BYPASS POSITION | EOH5-SDS-D1 | B-4F1005 SH. 711 | B25 | F B | BRN TAN | 9B 9A | 9 |
| 1 = BUS LINK IN BYPASS POSITION | EOH5-SDS-D1 | B-4F1005 SH. 711 | B26 | F B | RED TAN | 10B 10A | 10 |
| 1 = AIR PRESSURE LOW | EOH5-SDS-D1 | B-4F1005 SH. 711 | B27 | F B | ORN TAN | 11B 11A | 11 |
| EFDS : COIL CURRNT FLT DET: 1 = PF2L I2T FAULT | EFDS-D18 pc_nstxPF2L_i2tFlt_CALC | B-4F1005 SH. 1076 | B28 | F B | YLW TAN | 12B 12A | 12 |
| 1 = PF2L RIS OVRCURRENT TRIP | EFDS-D18 pc_nstxPF2L_risOvc_CALC | B-4F1005 SH. 1076 | B29 | F B | GRN TAN | 13B 13A | 13 |
| 1 = OH I2T FAULT | EFDS-D18 pc_nstxOH_i2tFlt_CALC | B-4F1005 SH. 1076 | B30 | F B | BLU TAN | 14B 14A | 14 |
| 1 = OH RIS OVRCURRENT TRIP | EFDS-D18 pc_nstxOH_risOvc_CALC | B-4F1005 SH. 1076 | B31 | F B | VIO TAN | 15B 15A | 15 |
| EFDS : 1 = TF COMP FAULT | EFDS-D28 & EFDM-IR-D6 & ETF-TTF pc_nstxTF_cmpFlt_BI | B-4F1005 SH. 1085 | B32 | F B | GRY TAN | 16B 16A | 16 |

| SLOT NO.: 8 | MODULE TYPE 302 DIGITAL OUTPUT |
| --- | --- |

| SIGNAL NAME | DEVICE ID | CONT. DWG | CROSS |  | CLR | PIN# | CH |
| --- | --- | --- | --- | --- | --- | --- | --- |
| SDS CNTRL FOR EF/VC CONVRTR: BIT 0 | EFVC-SDS-D1 | B-4F1005 SH. 490 | B33 | F B | BRN TAN | 3B 3A | 1 |
| BIT 1 | EFVC-SDS-D1 | B-4F1005 SH. 490 | B34 | F B | RED TAN | 4B 4A | 2 |
| BIT 2 | EFVC-SDS-D1 | B-4F1005 SH. 490 | B35 | F B | ORN TAN | 5B 5A | 3 |
| BIT 3 | EFVC-SDS-D1 | B-4F1005 SH. 490 | B36 | F B | YLW TAN | 6B 6A | 4 |
| SDS CNTRL FOR TF1 CONVRTR: BIT 0 | ETF1-SDS-D2 | B-4F1005 SH. 801 | B37 | F B | GRN TAN | 7B 7A | 5 |
| BIT 1 | ETF1-SDS-D2 | B-4F1005 SH. 801 | B38 | F B | BLU TAN | 8B 8A | 6 |
| BIT 2 | ETF1-SDS-D2 | B-4F1005 SH. 801 | B39 | F B | VIO TAN | 9B 9A | 7 |
| BIT 3 | ETF1-SDS-D2 | B-4F1005 SH. 801 | B40 | F B | GRY TAN | 10B 10A | 8 |
| BIT 4 | ETF1-SDS-D2 | B-4F1005 SH. 801 | B41 | F B | BRN TAN | 11B 11A | 9 |
| BIT 5 | ETF1-SDS-D2 | B-4F1005 SH. 801 | B42 | F B | RED TAN | 12B 12A | 10 |
| BIT 6 | ETF1-SDS-D2 | B-4F1005 SH. 801 | B43 | F B | ORN TAN | 13B 13A | 11 |
| BIT 7 | ETF1-SDS-D2 | B-4F1005 SH. 801 | B44 | F B | YLW TAN | 14B 14A | 12 |
| BIT 8 | ETF1-SDS-D2 | B-4F1005 SH. 801 | B45 | F B | GRN TAN | 15B 15A | 13 |
| BIT 9 | ETF1-SDS-D2 | B-4F1005 SH. 801 | B46 | F B | BLU TAN | 16B 16A | 14 |
|  |  |  | B47 | F B | VIO TAN | 17B 17A | 15 |
| TF TURN/TURN FAULT : 1 = TURN-TO-TURN FAULT | ETF-TTF |  | B48 | F B | GRY TAN | 18B 18A | 16 |

| SLOT NO.: 9 | MODULE TYPE 302 DIGITAL OUTPUT |
| --- | --- |

| SIGNAL NAME | DEVICE ID | CONT. DWG | CROSS |  | CLR | PIN# | CH |
| --- | --- | --- | --- | --- | --- | --- | --- |
| SDS CNTRL FOR OH6 CONVRTR: BIT 0 | EOH6-SDS-D1 | B-4F1005 SH. 712 | B49 | F B | BRN TAN | 3B 3A | 1 |
| BIT 1 | EOH6-SDS-D1 | B-4F1005 SH. 712 | B50 | F B | RED TAN | 4B 4A | 2 |
| BIT 2 | EOH6-SDS-D1 | B-4F1005 SH. 712 | B51 | F B | ORN TAN | 5B 5A | 3 |
| BIT 3 | EOH6-SDS-D1 | B-4F1005 SH. 712 | B52 | F B | YLW TAN | 6B 6A | 4 |
| SDS CNTRL FOR EF3 CONVRTR: BIT 0 | EEF3-SDS-D1 | B-4F1005 SH. 489 | B53 | F B | GRN TAN | 7B 7A | 5 |
| BIT 1 | EEF3-SDS-D1 | B-4F1005 SH. 489 | B54 | F B | BLU TAN | 8B 8A | 6 |
| BIT 2 | EEF3-SDS-D1 | B-4F1005 SH. 489 | B55 | F B | VIO TAN | 9B 9A | 7 |
| BIT 3 | EEF3-SDS-D1 | B-4F1005 SH. 489 | B56 | F B | GRY TAN | 10B 10A | 8 |
| SDS CNTRL FOR OH3 CONVRTR: BIT 0 | EOH3-SDS-D1 | B-4F1005 SH. 671 | B57 | F B | BRN TAN | 11B 11A | 9 |
| BIT 1 | EOH3-SDS-D1 | B-4F1005 SH. 671 | B58 | F B | RED TAN | 12B 12A | 10 |
| BIT 2 | EOH3-SDS-D1 | B-4F1005 SH. 671 | B59 | F B | ORN TAN | 13B 13A | 11 |
| BIT 3 | EOH3-SDS-D1 | B-4F1005 SH. 671 | B60 | F B | YLW TAN | 14B 14A | 12 |
| SDS CNTRL FOR OH5 CONVRTR: BIT 0 | EOH5-SDS-D1 | B-4F1005 SH. 711 | B61 | F B | GRN TAN | 15B 15A | 13 |
| BIT 1 | EOH5-SDS-D1 | B-4F1005 SH. 711 | B62 | F B | BLU TAN | 16B 16A | 14 |
| BIT 2 | EOH5-SDS-D1 | B-4F1005 SH. 711 | B63 | F B | VIO TAN | 17B 17A | 15 |
| BIT 3 | EOH5-SDS-D1 | B-4F1005 SH. 711 | B64 | F B | GRY TAN | 18B 18A | 16 |

| SLOT NO.: 10 | MODULE TYPE 320 ADC |
| --- | --- |

| SIGNAL NAME | DEVICE ID | CONT. DWG | CROSS |  | CLR | PIN# | CH |
| --- | --- | --- | --- | --- | --- | --- | --- |
| EFDS : FAULT DET MONITOR EF I2T Value | EFDM-IR-D1 pc_nstxPF2L_i2t_AI | B-4F1005 SH. 1085 | B65 | F B | BRN TAN | 1B 1A | 1 |
| EFDS : FAULT DET MONITOR HF I2T Value | EFDM-IR-D2 pc_nstxOH_i2t_AI | B-4F1005 SH. 1085 | B66 | F B | RED TAN | 2B 2A | 2 |
| EFDS : FAULT DET MONITOR OH I2T Value | EFDM-IR-D3 pc_nstxPF3U_i2t_AI | B-4F1005 SH. 1085 | B67 | F B | ORN TAN | 3B 3A | 3 |
| EFDS : FAULT DET MONITOR TF I2T Value | EFDM-IR-D4 pc_nstxTF_i2t_AI | B-4F1005 SH. 1085 | B68 | F B | YLW TAN | 4B 4A | 4 |
|  |  |  | B69 | F B | GRN TAN | 5B 5A | 5 |
|  |  |  | B70 | F B | BLU TAN | 6B 6A | 6 |
|  |  |  | B71 | F B | VIO TAN | 7B 7A | 7 |
|  |  |  | B72 | F B | GRY TAN | 8B 8A | 8 |
| EFDS : VC DELTA Not Used | EFDS-D24 | B-4F1005 SH. 1085 | B73 | F B | BRN TAN | 9B 9A | 9 |
| EFDS : VC I2T VC PF3L I2T | EFDS-D23 pc_nstxPF3L_i2t_AI | B-4F1005 SH. 1081 | B74 | F B | RED TAN | 10B 10A | 10 |
|  |  |  | B75 | F B | ORN TAN | 11B 11A | 11 |
|  |  |  | B76 | F B | YLW TAN | 12B 12A | 12 |
| EFDS : HI POT VOLTAGE | EFDS-D1 | B-4F1005 SH. 1065 | B77 | F B | GRN TAN | 13B 13A | 13 |
| EFDS : HI POT CURRENT | EFDS-D2 | B-4F1005 SH. 1065 | B78 | F B | BLU TAN | 14B 14A | 14 |
|  |  |  | B79 | F B | VIO TAN | 15B 15A | 15 |
|  |  |  | B80 | F B | GRY TAN | 16B 16A | 16 |

| SLOT NO.: 11 | MODULE TYPE 302 DIGITAL OUTPUT |
| --- | --- |

| SIGNAL NAME | DEVICE ID | CONT. DWG | CROSS |  | CLR | PIN# | CH |
| --- | --- | --- | --- | --- | --- | --- | --- |
| SDS CNTRL FOR EF4 CONVRTR: BIT 0 | EEF4-SDS-D1 | B-4F1005 SH. 524 | D1 | F B | BRN TAN | 3B 3A | 1 |
| BIT 1 | EEF4-SDS-D1 | B-4F1005 SH. 524 | D2 | F B | RED TAN | 4B 4A | 2 |
| BIT 2 | EEF4-SDS-D1 | B-4F1005 SH. 524 | D3 | F B | ORN TAN | 5B 5A | 3 |
| BIT 3 | EEF4-SDS-D1 | B-4F1005 SH. 524 | D4 | F B | YLW TAN | 6B 6A | 4 |
| EFDM : FAULT DET MONITOR: BIT 0 EF I2T Reset | EFDM-IR-D5 nstxPF3U i2t RESET | B-4F1005 SH. 1081 | D5 | F B | GRN TAN | 7B 7A | 5 |
| BIT 1 EF OvrCrnt Reset | EFDM-IR-D5 nstxPF3U ovCrnt RESET | B-4F1005 SH. 1081 | D6 | F B | BLU TAN | 8B 8A | 6 |
| BIT 2 HF I2T Reset | EFDM-IR-D5 nstxOH i2t RESET | B-4F1005 SH. 1081 | D7 | F B | VIO TAN | 9B 9A | 7 |
| BIT 3 HF OvrCrnt Reset | EFDM-IR-D5 nstxOH ovrCrnt RESET | B-4F1005 SH. 1081 | D8 | F B | GRY TAN | 10B 10A | 8 |
| BIT 4 OH I2T Reset | EFDM-IR-D5 nstxPF2L i2t RESET | B-4F1005 SH. 1081 | D9 | F B | BRN TAN | 11B 11A | 9 |
| BIT 5 OH OvrCrnt Reset | EFDM-IR-D5 nstxPF3L ovCrnt RESET | B-4F1005 SH. 1081 | D10 | F B | RED TAN | 12B 12A | 10 |
| BIT 6 TF I2T Reset | EFDM-IR-D5 nstxTF i2t RESET | B-4F1005 SH. 1081 | D11 | F B | ORN TAN | 13B 13A | 11 |
| BIT 7 TF OvrCrnt Reset | EFDM-IR-D5 nstxTF ovCrnt RESET | B-4F1005 SH. 1081 | D12 | F B | YLW TAN | 14B 14A | 12 |
| EF4/VC STATUS : BIT 0 VC I2T Reset | EFDS-21 nstxPF3L i2t RESET | B-4F1005 SH. 1076 | D13 | F B | GRN TAN | 15B 15A | 13 |
| BIT 1 VC OvrCrnt Reset | EFDS-21 nstxPF3L ovCrnt RESET | B-4F1005 SH. 1076 | D14 | F B | BLU TAN | 16B 16A | 14 |
| BIT 2 | EFDS-21 | B-4F1005 SH. 1076 | D15 | F B | VIO TAN | 17B 17A | 15 |
| TF GRND FAULT RESET - 1 | ETF-GFD-RST-1 |  | D16 | F B | GRY TAN | 18B 18A | 16 |

| SLOT NO.: 12 | MODULE TYPE 302 DIGITAL OUTPUT |
| --- | --- |

| SIGNAL NAME | DEVICE ID | CONT. DWG | CROSS |  | CLR | PIN# | CH |
| --- | --- | --- | --- | --- | --- | --- | --- |
| EFDM : FAULT DET MONITOR(D5), & HI POT CTL OUTPUT(D3) : BIT 0 | EFDS-D3 | B-4F1005 SH. 1067 | D17 | F B | BRN TAN | 3B 3A | 1 |
| BIT 1 | EFDS-D3 | B-4F1005 SH. 1067 | D18 | F B | RED TAN | 4B 4A | 2 |
| VC Halmar Conditioner Reset | EFDS-D3 & EFDS-D26 nstxPF3L HC RESET | B-4F1005 SH. 1067 | D19 | F B | ORN TAN | 5B 5A | 3 |
| TF Halmar Conditioner Reset | EFDS-D3 & EFDS-D26 nstxTF HC RESET | B-4F1005 SH. 1067 | D20 | F B | YLW TAN | 6B 6A | 4 |
| BIT 4 & D26 BIT 2 | EFDS-D3 & EFDS-D26 | B-4F1005 SH. 1067 | D21 | F B | GRN TAN | 7B 7A | 5 |
| EF Halmar Conditioner Reset | EFDS-D5 nstxPF3U HC RESET | B-4F1005 SH. 1067 | D22 | F B | BLU TAN | 8B 8A | 6 |
| BIT 1 | EFDS-D5 | B-4F1005 SH. 1067 | D23 | F B | VIO TAN | 9B 9A | 7 |
| BIT 2 | EFDS-D5 | B-4F1005 SH. 1067 | D24 | F B | GRY TAN | 10B 10A | 8 |
| BIT 3 | EFDS-D5 | B-4F1005 SH. 1067 | D25 | F B | BRN TAN | 11B 11A | 9 |
| BIT 4 | EFDS-D5 | B-4F1005 SH. 1067 | D26 | F B | RED TAN | 12B 12A | 10 |
| OH Halmar Conditioner Reset | EFDS-D5 & EFDS-D27 nstxPF2L HC RESET | B-4F1005 SH. 1067, 1081 | D27 | F B | ORN TAN | 13B 13A | 11 |
| HF Halmar Conditioner Reset | EFDS-D5 & EFDS-D27 nstxOH HC RESET | B-4F1005 SH. 1067, 1081 | D28 | F B | YLW TAN | 14B 14A | 12 |
| BIT 7 | EFDS-D5 | B-4F1005 SH. 1067 | D29 | F B | GRN TAN | 15B 15A | 13 |
| BIT 8 | EFDS-D5 | B-4F1005 SH. 1067 | D30 | F B | BLU TAN | 16B 16A | 14 |
| BIT 9 | EFDS-D5 | B-4F1005 SH. 1067 | D31 | F B | VIO TAN | 17B 17A | 15 |
| TF GRND FAULT RESET - 2 | ETF-GFD-RST-2 |  | D32 | F B | GRY TAN | 18B 18A | 16 |

| SLOT NO.: 13 | MODULE TYPE 322 DIGITAL INPUT |
| --- | --- |

| SIGNAL NAME | DEVICE ID | CONT. DWG | CROSS |  | CLR | PIN# | CH |
| --- | --- | --- | --- | --- | --- | --- | --- |
| EFDS : GRD FLT DET/TEST : 1 = EF/VC IN HIPOT POSITION | EFDS-D5 | B-4F1005 SH. 1067 | D33 | F B | BRN TAN | 1B 1A | 1 |
| 0 = EF/VC IN GRND'D POSITION | EFDS-D5 | B-4F1005 SH. 1067 | D34 | F B | RED TAN | 2B 2A | 2 |
| 1 = EF/VC GROUND FAULT | EFDS-D5 | B-4F1005 SH. 1067 | D35 | F B | ORN TAN | 3B 3A | 3 |
| 1 = OH IN HIPOT POSITION | EFDS-D5 | B-4F1005 SH. 1067 | D36 | F B | YLW TAN | 4B 4A | 4 |
| 0 = OH IN GRND'D POSITION | EFDS-D5 | B-4F1005 SH. 1067 | D37 | F B | GRN TAN | 5B 5A | 5 |
| 1 = OH GROUND FAULT | EFDS-D5 | B-4F1005 SH. 1067 | D38 | F B | BLU TAN | 6B 6A | 6 |
| 1 = TF IN HIPOT POSITION | EFDS-D5 | B-4F1005 SH. 1067 | D39 | F B | VIO TAN | 7B 7A | 7 |
| 0 = TF IN GRND'D POSITION | EFDS-D5 | B-4F1005 SH. 1067 | D40 | F B | GRY TAN | 8B 8A | 8 |
| 1 = TF GROUND FAULT, IR-D5 : DUMMY BIT | EFDS-D5 & EFDM-IR-D5 | B-4F1005 SH. 1067 | D41 | F B | BRN TAN | 9B 9A | 9 |
| 1 = HF IN HIPOT POSITION, IR-D5 : DUMMY BIT | EFDS-D5 & EFDM-IR-D5 | B-4F1005 SH. 1067 | D42 | F B | RED TAN | 10B 10A | 10 |
| 0 = HF IN GRND'D POSITION, IR-D5 : DUMMY BIT | EFDS-D5 & EFDM-IR-D5 | B-4F1005 SH. 1067 | D43 | F B | ORN TAN | 11B 11A | 11 |
| 1 = HF GROUND FAULT, IR-D5 : DUMMY BIT | EFDS-D5 & EFDM-IR-D5 | B-4F1005 SH. 1067 | D44 | F B | YLW TAN | 12B 12A | 12 |
| 0 = EFDS DOORS OPEN, IR-D5 : DUMMY BIT | EFDS-D5 & EFDM-IR-D5 | B-4F1005 SH. 1067 | D45 | F B | GRN TAN | 13B 13A | 13 |
| EFDS: STATUS BIT 0 EFDS 1 = OH Comp Fault | EFDS-D27 & EFDS-D26 & EFDM-IR-D5 pc_nstxPF2L_cmpFlt_BI | B-4F1005 SH. 1085 | D46 | F B | BLU TAN | 14B 14A | 14 |
| BIT 1, EFDS 1 = HF Comp Fault | EFDS-D27 & EFDS-D26 & EFDM-IR-D5 pc_nstxOH_cmpFlt_BI | B-4F1005 SH. 1085 | D47 | F B | VIO TAN | 15B 15A | 15 |
| BIT 2, EFDS 1 = EF Comp Fault | EFDS-D26 & EFDM-IR-D5 pc_nstxPF3U_cmpFlt_BI | B-4F1005 SH. 1085 | D48 | F B | GRY TAN | 16B 16A | 16 |

| SLOT NO.: 14 | MODULE TYPE 322 DIGITAL INPUT |
| --- | --- |

| SIGNAL NAME | DEVICE ID | CONT. DWG | CROSS |  | CLR | PIN# | CH |
| --- | --- | --- | --- | --- | --- | --- | --- |
| EFDS : CONTROL SYSTEM: 1 = EFDS IN CICADA MODE | EFDS-D6 | B-4F1005 SH. 1067 | D49 | F B | BRN TAN | 1B 1A | 1 |
| 1 = EFDS IN LOCAL MODE | EFDS-D6 | B-4F1005 SH. 1067 | D50 | F B | RED TAN | 2B 2A | 2 |
| 1 = EF/VC LOCAL CTL IN TEST MODE | EFDS-D6 | B-4F1005 SH. 1067 | D51 | F B | ORN TAN | 3B 3A | 3 |
| 1 = EF/VC LOCAL CTL IN NORMAL MODE | EFDS-D6 | B-4F1005 SH. 1067 | D52 | F B | YLW TAN | 4B 4A | 4 |
| 1 = OH LOCAL CTL IN TEST MODE | EFDS-D6 | B-4F1005 SH. 1067 | D53 | F B | GRN TAN | 5B 5A | 5 |
| 1 = OH LOCAL CTL IN NORMAL MODE | EFDS-D6 | B-4F1005 SH. 1067 | D54 | F B | BLU TAN | 6B 6A | 6 |
| 1 = HF LOCAL CTL IN TEST MODE | EFDS-D6 | B-4F1005 SH. 1067 | D55 | F B | VIO TAN | 7B 7A | 7 |
| 1 = HF LOCAL CTL IN NORMAL MODE | EFDS-D6 | B-4F1005 SH. 1067 | D56 | F B | GRY TAN | 8B 8A | 8 |
| 1 = TF LOCAL CTL IN TEST MODE | EFDS-D6 | B-4F1005 SH. 1067 | D57 | F B | BRN TAN | 9B 9A | 9 |
| 1 = TF LOCAL CTL IN NORMAL MODE | EFDS-D6 | B-4F1005 SH. 1067 | D58 | F B | RED TAN | 10B 10A | 10 |
| 1 = HI VOLTAGE ON | EFDS-D6 | B-4F1005 SH. 1067 | D59 | F B | ORN TAN | 11B 11A | 11 |
| 1 = HI VOLTAGE OFF | EFDS-D6 | B-4F1005 SH. 1067 | D60 | F B | YLW TAN | 12B 12A | 12 |
| EFDS : COIL CURRNT FLT DET: 1 = I2T FAULT ordering on CWD different | EFDS-D20 pc_nstxPF3U_i2tFlt_CALC | B-4F1005 SH. 1076 | D61 | F B | GRN TAN | 13B 13A | 13 |
| 1 = OVERCURRENT TRIP ordering on CWD different | EFDS-D20 pc_nstxPF3U_risOvc_CALC | B-4F1005 SH. 1076 | D62 | F B | BLU TAN | 14B 14A | 14 |
| 1 = TF I2T FAULT ordering on CWD different | EFDS-D20 pc_nstxTF_i2tFlt_CALC | B-4F1005 SH. 1076 | D63 | F B | VIO TAN | 15B 15A | 15 |
| 1 = TF OVERCURRENT TRIP ordering on CWD different | EFDS-D20 pc_nstxTF_risOvc_CALC | B-4F1005 SH. 1076 | D64 | F B | GRY TAN | 16B 16A | 16 |

| SLOT NO.: 16/18 | MODULE TYPE 908 TRANSIENT DIGITIZER, CHS 1-16 |
| --- | --- |

| SIGNAL NAME | DEVICE ID | CONT. DWG | CX | FCT | PIN# | CH |
| --- | --- | --- | --- | --- | --- | --- |
| EFDS SIGNAL – EFDS EEF PF1&TF Gnd Fault Current | EFDS-D9 | B-4F1005 SH. 1068 | D65 | + - SH | 2 3 1 | 1 |
| EFDS SIGNAL – EFDS EEF PF1&TF Gnd Fault Current | EFDS-D10 | B-4F1005 SH. 1068 | D66 | + - SH | 2 3 1 | 2 |
| EFDS SIGNAL – EFDS EEF PF2 Gnd Fault Current | EFDS-D11 | B-4F1005 SH. 1068 | D67 | + - SH | 2 3 1 | 3 |
| EFDS SIGNAL – EFDS EEF PF2 Gnd Fault Current | EFDS-D12 | B-4F1005 SH. 1068 | D68 | + - SH | 2 3 1 | 4 |
| EFDS SIGNAL – EFDS EEF CHI Gnd Fault Current | EFDS-D13 | B-4F1005 SH. 1068 | D69 | + - SH | 2 3 1 | 5 |
| EFDS SIGNAL – EFDS EEF CHI Gnd Fault Current | EFDS-D14 | B-4F1005 SH. 1068 | D70 | + - SH | 2 3 1 | 6 |
| EFDS SIGNAL – EFDS EEF OH Gnd Fault Current | EFDS-D15 | B-4F1005 SH. 1068 | D71 | + - SH | 2 3 1 | 7 |
| EFDS SIGNAL – EFDS EEF OH Gnd Fault Current | EFDS-D16 | B-4F1005 SH. 1068 | D72 | + - SH | 2 3 1 | 8 |
| TF1 SHUNT 1 | ESHNT-TF1 |  | D73 | + - SH | 2 3 1 | 9 |
| TF1 SHUNT 2 | ESHNT-TF2 |  | D74 | + - SH | 2 3 1 | 10 |
| TF1 SHUNT 3 | ESHNT-TF3 |  | D75 | + - SH | 2 3 1 | 11 |
| TF1 SHUNT 4 | ESHNT-TF4 |  | D76 | + - SH | 2 3 1 | 12 |
| EF SHUNT | ESHNT-EF1 |  | D77 | + - SH | 2 3 1 | 13 |
| OH SHUNT | ESHNT-OH1 |  | D78 | + - SH | 2 3 1 | 14 |
| VC SHUNT | ESHNT-VC1 |  | D79 | + - SH | 2 3 1 | 15 |
| HF SHUNT | ESHNT-HF1 |  | D80 | + - SH | 2 3 1 | 16 |

| SLOT NO.: 16/18 | MODULE TYPE 908 TRANSIENT DIGITIZER, CHS 17-32 |
| --- | --- |

| SIGNAL NAME | DEVICE ID | CONT. DWG | CX | FCT | PIN# | CH |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | + - SH | 2 3 1 | 17 |
|  |  |  |  | + - SH | 2 3 1 | 18 |
|  |  |  |  | + - SH | 2 3 1 | 19 |
|  |  |  |  | + - SH | 2 3 1 | 20 |
|  |  |  |  | + - SH | 2 3 1 | 21 |
|  |  |  |  | + - SH | 2 3 1 | 22 |
|  |  |  |  | + - SH | 2 3 1 | 23 |
|  |  |  |  | + - SH | 2 3 1 | 24 |
|  |  |  |  | + - SH | 2 3 1 | 25 |
|  |  |  |  | + - SH | 2 3 1 | 26 |
|  |  |  |  | + - SH | 2 3 1 | 27 |
|  |  |  |  | + - SH | 2 3 1 | 28 |
|  |  |  |  | + - SH | 2 3 1 | 29 |
|  |  |  |  | + - SH | 2 3 1 | 30 |
|  |  |  |  | + - SH | 2 3 1 | 31 |
|  |  |  |  | + - SH | 2 3 1 | 32 |

| SLOT NO.: 16/18 | MODULE TYPE 908 TRANSIENT DIGITIZER, CLK/TRIG |
| --- | --- |

| SIGNAL NAME | CONT. DWG | FCT | PIN# |
| --- | --- | --- | --- |
| TRIGGER INPUT - UPPER | FROM 404A, CH 0 OF 7 N = 21 DEVICE : PCTM-8-1 | + - SH | 2 3 1 |
| TRIGGER INPUT - LOWER |  | + - SH | 2 3 1 |
| CLOCK INPUT - UPPER |  | + - SH | 2 3 1 |
| CLOCK INPUT - LOWER |  | + - SH | 2 3 1 |

| SLOT NO.: 19 | MODULE TYPE 322 DIGITAL INPUT |
| --- | --- |

| SIGNAL NAME | DEVICE ID | CONT. DWG | CROSS |  | CLR | PIN# | CH |
| --- | --- | --- | --- | --- | --- | --- | --- |
| EF SYSTEM : BIT 0 | EEF-PSS-SYS-D3 | B-4F1005 SH. 588,589 | C1 | F B | BRN TAN | 1B 1A | 1 |
| BIT 1 | EEF-PSS-SYS-D3 | B-4F1005 SH. 588,589 | C2 | F B | RED TAN | 2B 2A | 2 |
| BIT 2 | EEF-PSS-SYS-D3 | B-4F1005 SH. 588,589 | C3 | F B | ORN TAN | 3B 3A | 3 |
| BIT 3 | EEF-PSS-SYS-D3 | B-4F1005 SH. 588,589 | C4 | F B | YLW TAN | 4B 4A | 4 |
| BIT 4 | EEF-PSS-SYS-D3 | B-4F1005 SH. 588,589 | C5 | F B | GRN TAN | 5B 5A | 5 |
| BIT 5 | EEF-PSS-SYS-D3 | B-4F1005 SH. 588,589 | C6 | F B | BLU TAN | 6B 6A | 6 |
| EF4/VC STATUS : BIT 0 OvrCrnt Fault ordering on CWD different | EFDS-21 pc_nstxPF3L_risOvc_CALC | B-4F1005 SH. 1076 | C7 | F B | VIO TAN | 7B 7A | 7 |
| BIT 1 I2T Fault ordering on CWD different | EFDS-21 pc_nstxPF3L_i2tFlt_CALC | B-4F1005 SH. 1076 | C8 | F B | GRY TAN | 8B 8A | 8 |
| BIT 2 | EFDS-21 | B-4F1005 SH. 1076 | C9 | F B | BRN TAN | 9B 9A | 9 |
|  |  |  | C10 | F B | RED TAN | 10B 10A | 10 |
| EFDS 1 = VC Comp Fault | EFDS-D29 pc_nstxPF3L_cmpFlt_BI | B-4F1005 SH. 1085 | C11 | F B | ORN TAN | 11B 11A | 11 |
|  |  |  | C12 | F B | YLW TAN | 12B 12A | 12 |
|  |  |  | C13 | F B | GRN TAN | 13B 13A | 13 |
|  |  |  | C14 | F B | BLU TAN | 14B 14A | 14 |
|  |  |  | C15 | F B | VIO TAN | 15B 15A | 15 |
|  |  |  | C16 | F B | GRY TAN | 16B 16A | 16 |

| SLOT NO.: 20/21 | MODULE TYPE 404A TIMING MODULE |
| --- | --- |

| SIGNAL NAME | DEVICE ID | CONT. DWG | CROSS |  | CLR | PIN# | CH |
| --- | --- | --- | --- | --- | --- | --- | --- |
| CLEAN EARTH |  |  |  | F B | BRN TAN | 1B 1A | CE |
| START TRIGGER FOR CRATE 8 TRANSIENT DIGITIZER | PCTM-8-1 | 908, N=16 TRIG INPUT |  | F B | RED TAN | 2B 2A | 1 |
| CLEAN EARTH |  |  |  | F B | ORN TAN | 3B 3A | CE |
|  |  |  |  | F B | YLW TAN | 4B 4A | 2 |
| CLEAN EARTH |  |  |  | F B | GRN TAN | 5B 5A | CE |
| SOP trigger #1 for PDP | pc_404c8n21ch3_SUB |  |  | F B | BLU TAN | 6B 6A | 3 |
| CLEAN EARTH |  |  |  | F B | VIO TAN | 7B 7A | CE |
| SOP Trigger #2 for PDP | pc_404c8n21ch4_SUB |  |  | F B | GRY TAN | 8B 8A | 4 |
| CLEAN EARTH |  |  |  | F B | BRN TAN | 9B 9A | CE |
|  |  |  |  | F B | RED TAN | 10B 10A | 5 |
| CLEAN EARTH |  |  |  | F B | ORN TAN | 11B 11A | CE |
|  |  |  |  | F B | YLW TAN | 12B 12A | 6 |
| CLEAN EARTH |  |  |  | F B | GRN TAN | 13B 13A | CE |
|  |  |  |  | F B | BLU TAN | 14B 14A | 7 |
| CLEAN EARTH |  |  |  | F B | VIO TAN | 15B 15A | CE |
|  |  |  |  | F B | GRY TAN | 16B 16A | 8 |