| CRATE LAYOUT DESCRIPTION |  |
| --- | --- |

| SLOT | CROSS-CX | MODULE DESCRIPTION & STRAPPING |
| --- | --- | --- |
| NSTX 1 | A01 - A16 | 322 16-BIT DIGITAL INPUT MODULE - ISOLATED CONTACT |
| NSTX 2 | A17 - A32 | 322 16-BIT DIGITAL INPUT MODULE - ISOLATED CONTACT |
| 3 | A33 - A48 | 322 16-BIT DIGITAL INPUT MODULE - ISOLATED CONTACT |
| NSTX 4 | A49 - A64 | 322 16-BIT DIGITAL INPUT MODULE - ISOLATED CONTACT |
| 5 | A65 - A80 | 322 16-BIT DIGITAL INPUT MODULE - ISOLATED CONTACT |
| NSTX 6 | B01 - B16 | 16-BIT DIGITAL OUTPUT MODULE - 302 RELAY OUTPUTS, MOMENTARY, NORM OPEN |
| NSTX 7 | B17 - B32 | 322 16-BIT DIGITAL INPUT MODULE - ISOLATED CONTACT |
| NSTX 8 | B33 - B48 | 322 16-BIT DIGITAL INPUT MODULE - ISOLATED CONTACT |
| NSTX 9 | B49 - B64 | 322 16-BIT DIGITAL INPUT MODULE - ISOLATED CONTACT |
| NSTX 10 | B65 - B80 | 322 16-BIT DIGITAL INPUT MODULE - ISOLATED CONTACT |
| 11 | ---- | 336 PC LINK REPEATER MODULE |
| NSTX 12 | D01 - D16 | 337 POWER SUPPLY CONTROLLER |
| 13 | D17 - D32 | 337 POWER SUPPLY CONTROLLER |
| 14 | D33 - D48 | 337 POWER SUPPLY CONTROLLER |
| 15 | D49 - D64 | 337 POWER SUPPLY CONTROLLER |
| 16 | ---- | 903 32 KW 12-BIT MEMORY [00000] |
| NSTX 17 | D65 - D80 | 32 CHANNEL TYPE 1 TRANSIENT DIGITIZER 908 +/- 5 VOLTS, 32 KW MEMORY, P2 CLOCK SOURCE |
| 18 | ---- | 908 (slot 2 of 3) |
| 19 | (T1) | 908 (slot 3 of 3) |
| NSTX 20 | (T1) | 404A 8 CHANNEL TIMING MODULE [E-STOP OFF] |
| 21 | ---- | 404A (slot 2 of 2) |
| 22 | ---- | 336 PC LINK REPEATER MODULE |
| 23 | ---- | 313 U-PORT ADAPTER (& FACILITY CLOCK) |
| 24/25 | ---- | 3952 L-2 CRATE CONTROLLER |

| SLOT NO.: 01 | MODULE TYPE 322 DIGITAL INPUT |
| --- | --- |

| SIGNAL NAME | DEVICE ID | CONT. DWG | CROSS |  | CLR | PIN# | CH |
| --- | --- | --- | --- | --- | --- | --- | --- |
| FEEDER BREAKER CONTROLS : 1 = LOCAL BREAKER TRIP CMD | EEF3-TRN-1+2 | B-4F1005 SH. 546 | A1 | F B | BRN TAN | 1B 1A | 1 |
| 1 = LOCAL BRKR CLOSE COMMAND | EEF3-TRN-1+2 | B-4F1005 SH. 546 | A2 | F B | RED TAN | 2B 2A | 2 |
| 1 = LOCAL CONTROL MODE | EEF3-TRN-1+2 | B-4F1005 SH. 546 | A3 | F B | ORN TAN | 3B 3A | 3 |
| 1 = CICADA CONTROL MODE | EEF3-TRN-1+2 | B-4F1005 SH. 546 | A4 | F B | YLW TAN | 4B 4A | 4 |
| 0 = PRIMARY RELAY TRIP | EEF3-TRN-1+2 | B-4F1005 SH. 546 | A5 | F B | GRN TAN | 5B 5A | 5 |
| 1 = SECONDARY RELAY TRIP | EEF3-TRN-1+2 | B-4F1005 SH. 546 | A6 | F B | BLU TAN | 6B 6A | 6 |
| FEEDER BREAKER CONTROLS : 1 = LOCAL BREAKER TRIP CMD | EEF4-TRN-1+2 | B-4F1005 SH. 546 | A7 | F B | VIO TAN | 7B 7A | 7 |
| 1 = LOCAL BRKR CLOSE COMMAND | EEF4-TRN-1+2 | B-4F1005 SH. 546 | A8 | F B | GRY TAN | 8B 8A | 8 |
| 1 = LOCAL CONTROL MODE | EEF4-TRN-1+2 | B-4F1005 SH. 546 | A9 | F B | BRN TAN | 9B 9A | 9 |
| 1 = CICADA CONTROL MODE | EEF4-TRN-1+2 | B-4F1005 SH. 546 | A10 | F B | RED TAN | 10B 10A | 10 |
| 0 = PRIMARY RELAY TRIP | EEF4-TRN-1+2 | B-4F1005 SH. 546 | A11 | F B | ORN TAN | 11B 11A | 11 |
| 1 = SECONDARY RELAY TRIP | EEF4-TRN-1+2 | B-4F1005 SH. 546 | A12 | F B | YLW TAN | 12B 12A | 12 |
|  |  |  | A13 | F B | GRN TAN | 13B 13A | 13 |
|  |  |  | A14 | F B | BLU TAN | 14B 14A | 14 |
|  |  |  | A15 | F B | VIO TAN | 15B 15A | 15 |
|  |  |  | A16 | F B | GRY TAN | 16B 16A | 16 |

| SLOT NO.: 02 | MODULE TYPE 322 DIGITAL INPUT |
| --- | --- |

| SIGNAL NAME | DEVICE ID | CONT. DWG | CROSS |  | CLR | PIN# | CH |
| --- | --- | --- | --- | --- | --- | --- | --- |
| EF3-1 CONVERTER TRANSFORMER: 0 = LIQUID LEVEL LOW | EEF3-TRN-1 | B-4F1005 SH. 475,545 | A17 | F B | BRN TAN | 1B 1A | 1 |
| 0 = LIQUID TEMP HI | EEF3-TRN-1 | B-4F1005 SH. 475,545 | A18 | F B | RED TAN | 2B 2A | 2 |
| 0 = WINDING TEMP HI | EEF3-TRN-1 | B-4F1005 SH. 475,545 | A19 | F B | ORN TAN | 3B 3A | 3 |
| 0 = TANK PRESSURE HI | EEF3-TRN-1 | B-4F1005 SH. 475,545 | A20 | F B | YLW TAN | 4B 4A | 4 |
| 0 = PRIMARY DISCONNECT SWITCH CLOSED | EEF3-TRN-1 | B-4F1005 SH. 475,545 | A21 | F B | GRN TAN | 5B 5A | 5 |
| 0 = THERMAL RELAY TRIP IMMINENT | EEF3-TRN-1 | B-4F1005 SH. 475,545 | A22 | F B | BLU TAN | 6B 6A | 6 |
| 1 = X WINDING OVERCURRENT TRIP | EEF3-TRN-1 | B-4F1005 SH. 475,545 | A23 | F B | VIO TAN | 7B 7A | 7 |
| 1 = Y WINDING OVERCURRENT TRIP | EEF3-TRN-1 | B-4F1005 SH. 475,545 | A24 | F B | GRY TAN | 8B 8A | 8 |
| EF3-2 CONVERTER TRANSFORMER: 0 = LIQUID LEVEL LOW | EEF3-TRN-2 | B-4F1005 SH. 475,545 | A25 | F B | BRN TAN | 9B 9A | 9 |
| 0 = LIQUID TEMP HI | EEF3-TRN-2 | B-4F1005 SH. 475,545 | A26 | F B | RED TAN | 10B 10A | 10 |
| 0 = WINDING TEMP HI | EEF3-TRN-2 | B-4F1005 SH. 475,545 | A27 | F B | ORN TAN | 11B 11A | 11 |
| 0 = TANK PRESSURE HI | EEF3-TRN-2 | B-4F1005 SH. 475,545 | A28 | F B | YLW TAN | 12B 12A | 12 |
| 0 = PRIMARY DISCONNECT SWITCH CLOSED | EEF3-TRN-2 | B-4F1005 SH. 475,545 | A29 | F B | GRN TAN | 13B 13A | 13 |
| 0 = THERMAL RELAY TRIP IMMINENT | EEF3-TRN-2 | B-4F1005 SH. 475,545 | A30 | F B | BLU TAN | 14B 14A | 14 |
| 1 = X WINDING OVERCURRENT TRIP | EEF3-TRN-2 | B-4F1005 SH. 475,545 | A31 | F B | VIO TAN | 15B 15A | 15 |
| 1 = Y WINDING OVERCURRENT TRIP | EEF3-TRN-2 | B-4F1005 SH. 475,545 | A32 | F B | GRY TAN | 16B 16A | 16 |

| SLOT NO.: 03 | MODULE TYPE 322 DIGITAL INPUT |
| --- | --- |

| SIGNAL NAME | DEVICE ID | CONT. DWG | CROSS |  | CLR | PIN# | CH |
| --- | --- | --- | --- | --- | --- | --- | --- |
| EF4-3 CONVERTER TRANSFORMER: 0 = LIQUID LEVEL LOW | EEF4-TRN-3 | B-4F1005 SH. 510,545 | A33 | F B | BRN TAN | 1B 1A | 1 |
| 0 = LIQUID TEMP HI | EEF4-TRN-3 | B-4F1005 SH. 510,545 | A34 | F B | RED TAN | 2B 2A | 2 |
| 0 = WINDING TEMP HI | EEF4-TRN-3 | B-4F1005 SH. 510,545 | A35 | F B | ORN TAN | 3B 3A | 3 |
| 0 = TANK PRESSURE HI | EEF4-TRN-3 | B-4F1005 SH. 510,545 | A36 | F B | YLW TAN | 4B 4A | 4 |
| 0 = PRIMARY DISCONNECT SWITCH CLOSED | EEF4-TRN-3 | B-4F1005 SH. 510,545 | A37 | F B | GRN TAN | 5B 5A | 5 |
| 0 = THERMAL RELAY TRIP IMMINENT | EEF4-TRN-3 | B-4F1005 SH. 510,545 | A38 | F B | BLU TAN | 6B 6A | 6 |
| 1 = X WINDING OVERCURRENT TRIP | EEF4-TRN-3 | B-4F1005 SH. 510,545 | A39 | F B | VIO TAN | 7B 7A | 7 |
| 1 = Y WINDING OVERCURRENT TRIP | EEF4-TRN-3 | B-4F1005 SH. 510,545 | A40 | F B | GRY TAN | 8B 8A | 8 |
| EF4-4 CONVERTER TRANSFORMER: 0 = LIQUID LEVEL LOW | EEF4-TRN-4 | B-4F1005 SH. 510,545 | A41 | F B | BRN TAN | 9B 9A | 9 |
| 0 = LIQUID TEMP HI | EEF4-TRN-4 | B-4F1005 SH. 510,545 | A42 | F B | RED TAN | 10B 10A | 10 |
| 0 = WINDING TEMP HI | EEF4-TRN-4 | B-4F1005 SH. 510,545 | A43 | F B | ORN TAN | 11B 11A | 11 |
| 0 = TANK PRESSURE HI | EEF4-TRN-4 | B-4F1005 SH. 510,545 | A44 | F B | YLW TAN | 12B 12A | 12 |
| 0 = PRIMARY DISCONNECT SWITCH CLOSED | EEF4-TRN-4 | B-4F1005 SH. 510,545 | A45 | F B | GRN TAN | 13B 13A | 13 |
| 0 = THERMAL RELAY TRIP IMMINENT | EEF4-TRN-4 | B-4F1005 SH. 510,545 | A46 | F B | BLU TAN | 14B 14A | 14 |
| 1 = X WINDING OVERCURRENT TRIP | EEF4-TRN-4 | B-4F1005 SH. 510,545 | A47 | F B | VIO TAN | 15B 15A | 15 |
| 1 = Y WINDING OVERCURRENT TRIP | EEF4-TRN-4 | B-4F1005 SH. 510,545 | A48 | F B | GRY TAN | 16B 16A | 16 |

| SLOT NO.: 04 | MODULE TYPE 322 DIGITAL INPUT |
| --- | --- |

| SIGNAL NAME | DEVICE ID | CONT. DWG | CROSS |  | CLR | PIN# | CH |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 = "A" DISCONNECT IN BYPASS POSITION, EF3-1 | EEF3-PSS-1C-D1 | B-4F1005 SH. 485,486 | A49 | F B | BRN TAN | 1B 1A | 1 |
| 1 = "A" DISCONNECT IN LINE POSITION | EEF3-PSS-1C-D1 | B-4F1005 SH. 485,486 | A50 | F B | RED TAN | 2B 2A | 2 |
| 1 = "B" DISCONNECT IN BYPASS POSITION | EEF3-PSS-1C-D1 | B-4F1005 SH. 485,486 | A51 | F B | ORN TAN | 3B 3A | 3 |
| 1 = "B" DISCONNECT IN LINE POSITION | EEF3-PSS-1C-D1 | B-4F1005 SH. 485,486 | A52 | F B | YLW TAN | 4B 4A | 4 |
| 1 = DOORS CLOSED | EEF3-PSS-1C-D1 | B-4F1005 SH. 485,486 | A53 | F B | GRN TAN | 5B 5A | 5 |
| 1 = "A" DISCONNECT IN BYPASS POSITION, EF3-2 | EEF3-PSS-2C-D1 | B-4F1005 SH. 487,488 | A54 | F B | BLU TAN | 6B 6A | 6 |
| 1 = "A" DISCONNECT IN LINE POSITION | EEF3-PSS-2C-D1 | B-4F1005 SH. 487,488 | A55 | F B | VIO TAN | 7B 7A | 7 |
| 1 = "B" DISCONNECT IN BYPASS POSITION | EEF3-PSS-2C-D1 | B-4F1005 SH. 487,488 | A56 | F B | GRY TAN | 8B 8A | 8 |
| 1 = "B" DISCONNECT IN LINE POSITION | EEF3-PSS-2C-D1 | B-4F1005 SH. 487,488 | A57 | F B | BRN TAN | 9B 9A | 9 |
| 1 = DOORS CLOSED | EEF3-PSS-2C-D1 | B-4F1005 SH. 487,488 | A58 | F B | RED TAN | 10B 10A | 10 |
|  |  |  | A59 | F B | ORN TAN | 11B 11A | 11 |
|  |  |  | A60 | F B | YLW TAN | 12B 12A | 12 |
|  |  |  | A61 | F B | GRN TAN | 13B 13A | 13 |
|  |  |  | A62 | F B | BLU TAN | 14B 14A | 14 |
|  |  |  | A63 | F B | VIO TAN | 15B 15A | 15 |
|  |  |  | A64 | F B | GRY TAN | 16B 16A | 16 |

| SLOT NO.: 05 | MODULE TYPE 322 DIGITAL INPUT |
| --- | --- |

| SIGNAL NAME | DEVICE ID | CONT. DWG | CROSS |  | CLR | PIN# | CH |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 = "A" DISCONNECT IN BYPASS POSITION, EF4-3 | EEF4-PSS-1C-D1 | B-4F1005 SH. 520,521 | A65 | F B | BRN TAN | 1B 1A | 1 |
| 1 = "A" DISCONNECT IN LINE POSITION | EEF4-PSS-1C-D1 | B-4F1005 SH. 520,521 | A66 | F B | RED TAN | 2B 2A | 2 |
| 1 = "B" DISCONNECT IN BYPASS POSITION | EEF4-PSS-1C-D1 | B-4F1005 SH. 520,521 | A67 | F B | ORN TAN | 3B 3A | 3 |
| 1 = "B" DISCONNECT IN LINE POSITION | EEF4-PSS-1C-D1 | B-4F1005 SH. 520,521 | A68 | F B | YLW TAN | 4B 4A | 4 |
| 1 = DOORS CLOSED | EEF4-PSS-1C-D1 | B-4F1005 SH. 520,521 | A69 | F B | GRN TAN | 5B 5A | 5 |
| 1 = "A" DISCONNECT IN BYPASS POSITION, EF4-4 | EEF4-PSS-2C-D1 | B-4F1005 SH. 522,523 | A70 | F B | BLU TAN | 6B 6A | 6 |
| 1 = "A" DISCONNECT IN LINE POSITION | EEF4-PSS-2C-D1 | B-4F1005 SH. 522,523 | A71 | F B | VIO TAN | 7B 7A | 7 |
| 1 = "B" DISCONNECT IN BYPASS POSITION | EEF4-PSS-2C-D1 | B-4F1005 SH. 522,523 | A72 | F B | GRY TAN | 8B 8A | 8 |
| 1 = "B" DISCONNECT IN LINE POSITION | EEF4-PSS-2C-D1 | B-4F1005 SH. 522,523 | A73 | F B | BRN TAN | 9B 9A | 9 |
| 1 = DOORS CLOSED | EEF4-PSS-2C-D1 | B-4F1005 SH. 522,523 | A74 | F B | RED TAN | 10B 10A | 10 |
|  |  |  | A75 | F B | ORN TAN | 11B 11A | 11 |
|  |  |  | A76 | F B | YLW TAN | 12B 12A | 12 |
|  |  |  | A77 | F B | GRN TAN | 13B 13A | 13 |
|  |  |  | A78 | F B | BLU TAN | 14B 14A | 14 |
|  |  |  | A79 | F B | VIO TAN | 15B 15A | 15 |
| 1 = PC Link 2 Active 0 = PC Link 2 Inactive |  | B-4F1005 SH. 522 | A80 | F B | GRY TAN | 16B 16A | 16 |

| SLOT NO.: 06 | MODULE TYPE 302 DIGITAL OUTPUT |
| --- | --- |

| SIGNAL NAME | DEVICE ID | CONT. DWG | CROSS |  | CLR | PIN# | CH |
| --- | --- | --- | --- | --- | --- | --- | --- |
| EF3-1 RESET COMMAND | EEF3-PSS-1C-D7 | B-4F1005 SH. 485,486 | B1 | F B | BRN TAN | 3B 3A | 1 |
| EF3-2 RESET COMMAND | EEF3-PSS-2C-D7 | B-4F1005 SH. 487,488 | B2 | F B | RED TAN | 4B 4A | 2 |
| EF4-1 RESET COMMAND | EEF4-PSS-1C-D7 | B-4F1005 SH. 520,521 | B3 | F B | ORN TAN | 5B 5A | 3 |
| EF4-2 RESET COMMAND | EEF4-PSS-2C-D7 | B-4F1005 SH. 522,523 | B4 | F B | YLW TAN | 6B 6A | 4 |
|  |  |  | B5 | F B | GRN TAN | 7B 7A | 5 |
|  |  |  | B6 | F B | BLU TAN | 8B 8A | 6 |
|  |  |  | B7 | F B | VIO TAN | 9B 9A | 7 |
|  |  |  | B8 | F B | GRY TAN | 10B 10A | 8 |
|  |  |  | B9 | F B | BRN TAN | 11B 11A | 9 |
|  |  |  | B10 | F B | RED TAN | 12B 12A | 10 |
|  |  |  | B11 | F B | ORN TAN | 13B 13A | 11 |
|  |  |  | B12 | F B | YLW TAN | 14B 14A | 12 |
|  |  |  | B13 | F B | GRN TAN | 15B 15A | 13 |
|  |  |  | B14 | F B | BLU TAN | 16B 16A | 14 |
|  |  |  | B15 | F B | VIO TAN | 17B 17A | 15 |
|  |  |  | B16 | F B | GRY TAN | 18B 18A | 16 |

| SLOT NO.: 07 | MODULE TYPE 322 DIGITAL INPUT |
| --- | --- |

| SIGNAL NAME | DEVICE ID | CONT. DWG | CROSS |  | CLR | PIN# | CH |
| --- | --- | --- | --- | --- | --- | --- | --- |
| EF3-1 : FAULT DETECTOR BIT 0 | EEF3-PSS-1C-D2 & EEF3-PSS-1C-D6 | B-4F1005 SH. 485,486 | B17 | F B | BRN TAN | 1B 1A | 1 |
| FAULT DETECTOR BIT 1 | EEF3-PSS-1C-D2 & EEF3-PSS-1C-D6 | B-4F1005 SH. 485,486 | B18 | F B | RED TAN | 2B 2A | 2 |
| FAULT DETECTOR BIT 2 | EEF3-PSS-1C-D2 & EEF3-PSS-1C-D6 | B-4F1005 SH. 485,486 | B19 | F B | ORN TAN | 3B 3A | 3 |
| FAULT DETECTOR BIT 3 | EEF3-PSS-1C-D2 & EEF3-PSS-1C-D6 | B-4F1005 SH. 485,486 | B20 | F B | YLW TAN | 4B 4A | 4 |
| FAULT DETECTOR BIT 4 | EEF3-PSS-1C-D3 & EEF3-PSS-1C-D6 | B-4F1005 SH. 485,486 | B21 | F B | GRN TAN | 5B 5A | 5 |
| FAULT DETECTOR BIT 5 | EEF3-PSS-1C-D3 & EEF3-PSS-1C-D6 | B-4F1005 SH. 485,486 | B22 | F B | BLU TAN | 6B 6A | 6 |
| FAULT DETECTOR BIT 6 | EEF3-PSS-1C-D3 & EEF3-PSS-1C-D6 | B-4F1005 SH. 485,486 | B23 | F B | VIO TAN | 7B 7A | 7 |
| FAULT DETECTOR BIT 7 | EEF3-PSS-1C-D3 & EEF3-PSS-1C-D6 | B-4F1005 SH. 485,486 | B24 | F B | GRY TAN | 8B 8A | 8 |
| FAULT DETECTOR BIT 8 | EEF3-PSS-1C-D4 & EEF3-PSS-1C-D6 | B-4F1005 SH. 485,486 | B25 | F B | BRN TAN | 9B 9A | 9 |
| FAULT DETECTOR BIT 9 | EEF3-PSS-1C-D4 & EEF3-PSS-1C-D6 | B-4F1005 SH. 485,486 | B26 | F B | RED TAN | 10B 10A | 10 |
| FAULT DETECTOR BIT 10 | EEF3-PSS-1C-D4 & EEF3-PSS-1C-D6 | B-4F1005 SH. 485,486 | B27 | F B | ORN TAN | 11B 11A | 11 |
| FAULT DETECTOR BIT 11 | EEF3-PSS-1C-D4 & EEF3-PSS-1C-D6 | B-4F1005 SH. 485,486 | B28 | F B | YLW TAN | 12B 12A | 12 |
| FAULT DETECTOR BIT 12 | EEF3-PSS-1C-D5 & EEF3-PSS-1C-D6 | B-4F1005 SH. 485,486 | B29 | F B | GRN TAN | 13B 13A | 13 |
| FAULT DETECTOR BIT 13 | EEF3-PSS-1C-D5 & EEF3-PSS-1C-D6 | B-4F1005 SH. 485,486 | B30 | F B | BLU TAN | 14B 14A | 14 |
| FAULT DETECTOR BIT 14 | EEF3-PSS-1C-D5 & EEF3-PSS-1C-D6 | B-4F1005 SH. 485,486 | B31 | F B | VIO TAN | 15B 15A | 15 |
| FAULT DETECTOR BIT 15 | EEF3-PSS-1C-D5 & EEF3-PSS-1C-D6 | B-4F1005 SH. 485,486 | B32 | F B | GRY TAN | 16B 16A | 16 |

| SLOT NO.: 08 | MODULE TYPE 322 DIGITAL INPUT |
| --- | --- |

| SIGNAL NAME | DEVICE ID | CONT. DWG | CROSS |  | CLR | PIN# | CH |
| --- | --- | --- | --- | --- | --- | --- | --- |
| EF3-2 : FAULT DETECTOR BIT 0 | EEF3-PSS-2C-D2 & EEF3-PSS-2C-D6 | B-4F1005 SH. 487,488 | B33 | F B | BRN TAN | 1B 1A | 1 |
| FAULT DETECTOR BIT 1 | EEF3-PSS-2C-D2 & EEF3-PSS-2C-D6 | B-4F1005 SH. 487,488 | B34 | F B | RED TAN | 2B 2A | 2 |
| FAULT DETECTOR BIT 2 | EEF3-PSS-2C-D2 & EEF3-PSS-2C-D6 | B-4F1005 SH. 487,488 | B35 | F B | ORN TAN | 3B 3A | 3 |
| FAULT DETECTOR BIT 3 | EEF3-PSS-2C-D2 & EEF3-PSS-2C-D6 | B-4F1005 SH. 487,488 | B36 | F B | YLW TAN | 4B 4A | 4 |
| FAULT DETECTOR BIT 4 | EEF3-PSS-2C-D3 & EEF3-PSS-2C-D6 | B-4F1005 SH. 487,488 | B37 | F B | GRN TAN | 5B 5A | 5 |
| FAULT DETECTOR BIT 5 | EEF3-PSS-2C-D3 & EEF3-PSS-2C-D6 | B-4F1005 SH. 487,488 | B38 | F B | BLU TAN | 6B 6A | 6 |
| FAULT DETECTOR BIT 6 | EEF3-PSS-2C-D3 & EEF3-PSS-2C-D6 | B-4F1005 SH. 487,488 | B39 | F B | VIO TAN | 7B 7A | 7 |
| FAULT DETECTOR BIT 7 | EEF3-PSS-2C-D3 & EEF3-PSS-2C-D6 | B-4F1005 SH. 487,488 | B40 | F B | GRY TAN | 8B 8A | 8 |
| FAULT DETECTOR BIT 8 | EEF3-PSS-2C-D4 & EEF3-PSS-2C-D6 | B-4F1005 SH. 487,488 | B41 | F B | BRN TAN | 9B 9A | 9 |
| FAULT DETECTOR BIT 9 | EEF3-PSS-2C-D4 & EEF3-PSS-2C-D6 | B-4F1005 SH. 487,488 | B42 | F B | RED TAN | 10B 10A | 10 |
| FAULT DETECTOR BIT 10 | EEF3-PSS-2C-D4 & EEF3-PSS-2C-D6 | B-4F1005 SH. 487,488 | B43 | F B | ORN TAN | 11B 11A | 11 |
| FAULT DETECTOR BIT 11 | EEF3-PSS-2C-D4 & EEF3-PSS-2C-D6 | B-4F1005 SH. 487,488 | B44 | F B | YLW TAN | 12B 12A | 12 |
| FAULT DETECTOR BIT 12 | EEF3-PSS-2C-D5 & EEF3-PSS-2C-D6 | B-4F1005 SH. 487,488 | B45 | F B | GRN TAN | 13B 13A | 13 |
| FAULT DETECTOR BIT 13 | EEF3-PSS-2C-D5 & EEF3-PSS-2C-D6 | B-4F1005 SH. 487,488 | B46 | F B | BLU TAN | 14B 14A | 14 |
| FAULT DETECTOR BIT 14 | EEF3-PSS-2C-D5 & EEF3-PSS-2C-D6 | B-4F1005 SH. 487,488 | B47 | F B | VIO TAN | 15B 15A | 15 |
| FAULT DETECTOR BIT 15 | EEF3-PSS-2C-D5 & EEF3-PSS-2C-D6 | B-4F1005 SH. 487,488 | B48 | F B | GRY TAN | 16B 16A | 16 |

| SLOT NO.: 09 | MODULE TYPE 322 DIGITAL INPUT |
| --- | --- |

| SIGNAL NAME | DEVICE ID | CONT. DWG | CROSS |  | CLR | PIN# | CH |
| --- | --- | --- | --- | --- | --- | --- | --- |
| EF4-3?: FAULT DETECTOR BIT 0 | EEF4-PSS-1C-D2 & EEF4-PSS-1C-D6 | B-4F1005 SH. 520,521 | B49 | F B | BRN TAN | 1B 1A | 1 |
| FAULT DETECTOR BIT 1 | EEF4-PSS-1C-D2 & EEF4-PSS-1C-D6 | B-4F1005 SH. 520,521 | B50 | F B | RED TAN | 2B 2A | 2 |
| FAULT DETECTOR BIT 2 | EEF4-PSS-1C-D2 & EEF4-PSS-1C-D6 | B-4F1005 SH. 520,521 | B51 | F B | ORN TAN | 3B 3A | 3 |
| FAULT DETECTOR BIT 3 | EEF4-PSS-1C-D2 & EEF4-PSS-1C-D6 | B-4F1005 SH. 520,521 | B52 | F B | YLW TAN | 4B 4A | 4 |
| FAULT DETECTOR BIT 4 | EEF4-PSS-1C-D3 & EEF4-PSS-1C-D6 | B-4F1005 SH. 520,521 | B53 | F B | GRN TAN | 5B 5A | 5 |
| FAULT DETECTOR BIT 5 | EEF4-PSS-1C-D3 & EEF4-PSS-1C-D6 | B-4F1005 SH. 520,521 | B54 | F B | BLU TAN | 6B 6A | 6 |
| FAULT DETECTOR BIT 6 | EEF4-PSS-1C-D3 & EEF4-PSS-1C-D6 | B-4F1005 SH. 520,521 | B55 | F B | VIO TAN | 7B 7A | 7 |
| FAULT DETECTOR BIT 7 | EEF4-PSS-1C-D3 & EEF4-PSS-1C-D6 | B-4F1005 SH. 520,521 | B56 | F B | GRY TAN | 8B 8A | 8 |
| FAULT DETECTOR BIT 8 | EEF4-PSS-1C-D4 & EEF4-PSS-1C-D6 | B-4F1005 SH. 520,521 | B57 | F B | BRN TAN | 9B 9A | 9 |
| FAULT DETECTOR BIT 9 | EEF4-PSS-1C-D4 & EEF4-PSS-1C-D6 | B-4F1005 SH. 520,521 | B58 | F B | RED TAN | 10B 10A | 10 |
| FAULT DETECTOR BIT 10 | EEF4-PSS-1C-D4 & EEF4-PSS-1C-D6 | B-4F1005 SH. 520,521 | B59 | F B | ORN TAN | 11B 11A | 11 |
| FAULT DETECTOR BIT 11 | EEF4-PSS-1C-D4 & EEF4-PSS-1C-D6 | B-4F1005 SH. 520,521 | B60 | F B | YLW TAN | 12B 12A | 12 |
| FAULT DETECTOR BIT 12 | EEF4-PSS-1C-D5 & EEF4-PSS-1C-D6 | B-4F1005 SH. 520,521 | B61 | F B | GRN TAN | 13B 13A | 13 |
| FAULT DETECTOR BIT 13 | EEF4-PSS-1C-D5 & EEF4-PSS-1C-D6 | B-4F1005 SH. 520,521 | B62 | F B | BLU TAN | 14B 14A | 14 |
| FAULT DETECTOR BIT 14 | EEF4-PSS-1C-D5 & EEF4-PSS-1C-D6 | B-4F1005 SH. 520,521 | B63 | F B | VIO TAN | 15B 15A | 15 |
| FAULT DETECTOR BIT 15 | EEF4-PSS-1C-D5 & EEF4-PSS-1C-D6 | B-4F1005 SH. 520,521 | B64 | F B | GRY TAN | 16B 16A | 16 |

| SLOT NO.: 10 | MODULE TYPE 322 DIGITAL INPUT |
| --- | --- |

| SIGNAL NAME | DEVICE ID | CONT. DWG | CROSS |  | CLR | PIN# | CH |
| --- | --- | --- | --- | --- | --- | --- | --- |
| EF4-4?: FAULT DETECTOR BIT 0 | EEF4-PSS-2C-D2 & EEF4-PSS-2C-D6 | B-4F1005 SH. 522,523 | B65 | F B | BRN TAN | 1B 1A | 1 |
| FAULT DETECTOR BIT 1 | EEF4-PSS-2C-D2 & EEF4-PSS-2C-D6 | B-4F1005 SH. 522,523 | B66 | F B | RED TAN | 2B 2A | 2 |
| FAULT DETECTOR BIT 2 | EEF4-PSS-2C-D2 & EEF4-PSS-2C-D6 | B-4F1005 SH. 522,523 | B67 | F B | ORN TAN | 3B 3A | 3 |
| FAULT DETECTOR BIT 3 | EEF4-PSS-2C-D2 & EEF4-PSS-2C-D6 | B-4F1005 SH. 522,523 | B68 | F B | YLW TAN | 4B 4A | 4 |
| FAULT DETECTOR BIT 4 | EEF4-PSS-2C-D3 & EEF4-PSS-2C-D6 | B-4F1005 SH. 522,523 | B69 | F B | GRN TAN | 5B 5A | 5 |
| FAULT DETECTOR BIT 5 | EEF4-PSS-2C-D3 & EEF4-PSS-2C-D6 | B-4F1005 SH. 522,523 | B70 | F B | BLU TAN | 6B 6A | 6 |
| FAULT DETECTOR BIT 6 | EEF4-PSS-2C-D3 & EEF4-PSS-2C-D6 | B-4F1005 SH. 522,523 | B71 | F B | VIO TAN | 7B 7A | 7 |
| FAULT DETECTOR BIT 7 | EEF4-PSS-2C-D3 & EEF4-PSS-2C-D6 | B-4F1005 SH. 522,523 | B72 | F B | GRY TAN | 8B 8A | 8 |
| FAULT DETECTOR BIT 8 | EEF4-PSS-2C-D4 & EEF4-PSS-2C-D6 | B-4F1005 SH. 522,523 | B73 | F B | BRN TAN | 9B 9A | 9 |
| FAULT DETECTOR BIT 9 | EEF4-PSS-2C-D4 & EEF4-PSS-2C-D6 | B-4F1005 SH. 522,523 | B74 | F B | RED TAN | 10B 10A | 10 |
| FAULT DETECTOR BIT 10 | EEF4-PSS-2C-D4 & EEF4-PSS-2C-D6 | B-4F1005 SH. 522,523 | B75 | F B | ORN TAN | 11B 11A | 11 |
| FAULT DETECTOR BIT 11 | EEF4-PSS-2C-D4 & EEF4-PSS-2C-D6 | B-4F1005 SH. 522,523 | B76 | F B | YLW TAN | 12B 12A | 12 |
| FAULT DETECTOR BIT 12 | EEF4-PSS-2C-D5 & EEF4-PSS-2C-D6 | B-4F1005 SH. 522,523 | B77 | F B | GRN TAN | 13B 13A | 13 |
| FAULT DETECTOR BIT 13 | EEF4-PSS-2C-D5 & EEF4-PSS-2C-D6 | B-4F1005 SH. 522,523 | B78 | F B | BLU TAN | 14B 14A | 14 |
| FAULT DETECTOR BIT 14 | EEF4-PSS-2C-D5 & EEF4-PSS-2C-D6 | B-4F1005 SH. 522,523 | B79 | F B | VIO TAN | 15B 15A | 15 |
| FAULT DETECTOR BIT 15 | EEF4-PSS-2C-D5 & EEF4-PSS-2C-D6 | B-4F1005 SH. 522,523 | B80 | F B | GRY TAN | 16B 16A | 16 |

| SLOT NO.: 11 | MODULE TYPE 336 PC_LINK REPEATER |
| --- | --- |

| DESCRIPTION | CONMMENT | CONT'D DWG |
| --- | --- | --- |
| CONTROL FOR POWER SUPPLY : __EF3__________________________________ |
| HOUSE ADDRESS (HA) = _22_ |  | N/A |
| SUBAGGREGATE HOUSE ADDRESS = _3D |  | N/A |
| PC LINK INPUT |  |  |
| PC LINK OUTPUT |  |  |
| I/O TO POWER SUPPLY CONTROLLER |  |  |

| SLOT NO.: 12 | MODULE TYPE 337 POWER SUPPLY CONTROLLER |
| --- | --- |

| DESCRIPTION | CONMMENT | CONT'D DWG |
| --- | --- | --- |
| CONTROL FOR POWER SUPPLY : __EF3-1__________________________________ |
| POWER SUPPLY ADDRESS (PSA) = _1_ |  | N/A |
| LINK I/O (UPPER CONNECTOR) |  |  |
| LINK I/O (LOWER CONNECTOR) |  |  |
| SIGNAL NAME | CONT. DWG | CROSS |  | CLR | PIN# | BIT |
| FIRING ANGLE 20 - LSB |  | D1 | F B | BRN TAN | 1B 1A | 1 |
| FIRING ANGLE 21 |  | D2 | F B | RED TAN | 2B 2A | 2 |
| FIRING ANGLE 22 |  | D3 | F B | ORN TAN | 3B 3A | 3 |
| FIRING ANGLE 23 |  | D4 | F B | YLW TAN | 4B 4A | 4 |
| FIRING ANGLE 24 |  | D5 | F B | GRN TAN | 5B 5A | 5 |
| FIRING ANGLE 25 |  | D6 | F B | BLU TAN | 6B 6A | 6 |
| FIRING ANGLE 26 |  | D7 | F B | VIO TAN | 7B 7A | 7 |
| FIRING ANGLE 27 - MSB |  | D8 | F B | GRY TAN | 8B 8A | 8 |
| "CONVERT" MODE |  | D9 | F B | BRN TAN | 9B 9A | 9 |
| "CYCLIC BYPASS" MODE |  | D10 | F B | RED TAN | 10B 10A | 10 |
| "BLOCK BYPASS" MODE |  | D11 | F B | ORN TAN | 11B 11A | 11 |
| SPARE - BIT 12 |  | D12 | F B | YLW TAN | 12B 12A | 12 |
| SPARE - BIT 13 |  | D13 | F B | GRN TAN | 13B 13A | 13 |
| SPARE - BIT 14 |  | D14 | F B | BLU TAN | 14B 14A | 14 |
| SPARE |  | D15 | F B | VIO TAN | 15B 15A | 15 |
| READY |  | D16 | F B | GRY TAN | 16B 16A | 16 |

| SLOT NO.: 13 | MODULE TYPE 337 POWER SUPPLY CONTROLLER |
| --- | --- |

| DESCRIPTION | CONMMENT | CONT'D DWG |
| --- | --- | --- |
| CONTROL FOR POWER SUPPLY : __EF3-2__________________________________ |
| POWER SUPPLY ADDRESS (PSA) = _2__ |  | N/A |
| LINK I/O (UPPER CONNECTOR) |  |  |
| LINK I/O (LOWER CONNECTOR) |  |  |
| SIGNAL NAME | CONT. DWG | CROSS |  | CLR | PIN# | BIT |
| FIRING ANGLE 20 - LSB |  | D17 | F B | BRN TAN | 1B 1A | 1 |
| FIRING ANGLE 21 |  | D18 | F B | RED TAN | 2B 2A | 2 |
| FIRING ANGLE 22 |  | D19 | F B | ORN TAN | 3B 3A | 3 |
| FIRING ANGLE 23 |  | D20 | F B | YLW TAN | 4B 4A | 4 |
| FIRING ANGLE 24 |  | D21 | F B | GRN TAN | 5B 5A | 5 |
| FIRING ANGLE 25 |  | D22 | F B | BLU TAN | 6B 6A | 6 |
| FIRING ANGLE 26 |  | D23 | F B | VIO TAN | 7B 7A | 7 |
| FIRING ANGLE 27 - MSB |  | D24 | F B | GRY TAN | 8B 8A | 8 |
| "CONVERT" MODE |  | D25 | F B | BRN TAN | 9B 9A | 9 |
| "CYCLIC BYPASS" MODE |  | D26 | F B | RED TAN | 10B 10A | 10 |
| "BLOCK BYPASS" MODE |  | D27 | F B | ORN TAN | 11B 11A | 11 |
| SPARE - BIT 12 |  | D28 | F B | YLW TAN | 12B 12A | 12 |
| SPARE - BIT 13 |  | D29 | F B | GRN TAN | 13B 13A | 13 |
| SPARE - BIT 14 |  | D30 | F B | BLU TAN | 14B 14A | 14 |
| SPARE |  | D31 | F B | VIO TAN | 15B 15A | 15 |
| READY |  | D32 | F B | GRY TAN | 16B 16A | 16 |

| SLOT NO.: 14 | MODULE TYPE 337 POWER SUPPLY CONTROLLER |
| --- | --- |

| DESCRIPTION | CONMMENT | CONT'D DWG |
| --- | --- | --- |
| CONTROL FOR POWER SUPPLY : __EF4-1__________________________________ |
| POWER SUPPLY ADDRESS (PSA) = __3__ |  | N/A |
| LINK I/O (UPPER CONNECTOR) |  |  |
| LINK I/O (LOWER CONNECTOR) |  |  |
| SIGNAL NAME | CONT. DWG | CROSS |  | CLR | PIN# | BIT |
| FIRING ANGLE 20 - LSB |  | D33 | F B | BRN TAN | 1B 1A | 1 |
| FIRING ANGLE 21 |  | D34 | F B | RED TAN | 2B 2A | 2 |
| FIRING ANGLE 22 |  | D35 | F B | ORN TAN | 3B 3A | 3 |
| FIRING ANGLE 23 |  | D36 | F B | YLW TAN | 4B 4A | 4 |
| FIRING ANGLE 24 |  | D37 | F B | GRN TAN | 5B 5A | 5 |
| FIRING ANGLE 25 |  | D38 | F B | BLU TAN | 6B 6A | 6 |
| FIRING ANGLE 26 |  | D39 | F B | VIO TAN | 7B 7A | 7 |
| FIRING ANGLE 27 - MSB |  | D40 | F B | GRY TAN | 8B 8A | 8 |
| "CONVERT" MODE |  | D41 | F B | BRN TAN | 9B 9A | 9 |
| "CYCLIC BYPASS" MODE |  | D42 | F B | RED TAN | 10B 10A | 10 |
| "BLOCK BYPASS" MODE |  | D43 | F B | ORN TAN | 11B 11A | 11 |
| SPARE - BIT 12 |  | D44 | F B | YLW TAN | 12B 12A | 12 |
| SPARE - BIT 13 |  | D45 | F B | GRN TAN | 13B 13A | 13 |
| SPARE - BIT 14 |  | D46 | F B | BLU TAN | 14B 14A | 14 |
| SPARE |  | D47 | F B | VIO TAN | 15B 15A | 15 |
| READY |  | D48 | F B | GRY TAN | 16B 16A | 16 |

| SLOT NO.: 15 | MODULE TYPE 337 POWER SUPPLY CONTROLLER |
| --- | --- |

| DESCRIPTION | CONMMENT | CONT'D DWG |
| --- | --- | --- |
| CONTROL FOR POWER SUPPLY : __EF4-2__________________________________ |
| POWER SUPPLY ADDRESS (PSA) = _4__ |  | N/A |
| LINK I/O (UPPER CONNECTOR) |  |  |
| LINK I/O (LOWER CONNECTOR) |  |  |
| SIGNAL NAME | CONT. DWG | CROSS |  | CLR | PIN# | BIT |
| FIRING ANGLE 20 - LSB |  | D49 | F B | BRN TAN | 1B 1A | 1 |
| FIRING ANGLE 21 |  | D50 | F B | RED TAN | 2B 2A | 2 |
| FIRING ANGLE 22 |  | D51 | F B | ORN TAN | 3B 3A | 3 |
| FIRING ANGLE 23 |  | D52 | F B | YLW TAN | 4B 4A | 4 |
| FIRING ANGLE 24 |  | D53 | F B | GRN TAN | 5B 5A | 5 |
| FIRING ANGLE 25 |  | D54 | F B | BLU TAN | 6B 6A | 6 |
| FIRING ANGLE 26 |  | D55 | F B | VIO TAN | 7B 7A | 7 |
| FIRING ANGLE 27 - MSB |  | D56 | F B | GRY TAN | 8B 8A | 8 |
| "CONVERT" MODE |  | D57 | F B | BRN TAN | 9B 9A | 9 |
| "CYCLIC BYPASS" MODE |  | D58 | F B | RED TAN | 10B 10A | 10 |
| "BLOCK BYPASS" MODE |  | D59 | F B | ORN TAN | 11B 11A | 11 |
| SPARE - BIT 12 |  | D60 | F B | YLW TAN | 12B 12A | 12 |
| SPARE - BIT 13 |  | D61 | F B | GRN TAN | 13B 13A | 13 |
| SPARE - BIT 14 |  | D62 | F B | BLU TAN | 14B 14A | 14 |
| SPARE |  | D63 | F B | VIO TAN | 15B 15A | 15 |
| READY | To D64 via TB 1 F/B on B-AE4227. See B4F1005 Sh. 522 | D64 | F B | GRY TAN | 16B 16A | 16 |

| SLOT NO.: 17/19 | MODULE TYPE 908 TRANSIENT DIGITIZER, CHS 1-16 |
| --- | --- |

| SIGNAL NAME | DEVICE ID | CONT. DWG | CX | FCT | PIN# | CH |
| --- | --- | --- | --- | --- | --- | --- |
| PF1AL-PSS-2S CURRENT 8 V = 24 KA (4.99 K IN-LINE RESISTORS DIVIDE INPUT VOLTAGE BY 2) | pc_pf1al_pss_2s_i | B-4F1005 SH. 485,486 | D65 | + - SH | 2 3 1 | 1 |
| PF1AL-PSS-1S CURRENT | pc_pf1al_pss_1s_i | B-4F1005 SH. 485,486 | D66 | + - SH | 2 3 1 | 2 |
| PF1AL-PSS-2S VOLTAGE 10 V = 1500 VOLTS (DITTO 4.99 K) | pc_pf1al_pss_2s_v | B-4F1005 SH. 485,486 | D67 | + - SH | 2 3 1 | 3 |
| PF1AL-PSS-1S VOLTAGE | pc_pf1al_pss_1s_v | B-4F1005 SH. 485,486 | D68 | + - SH | 2 3 1 | 4 |
|  |  | B-4F1005 SH. 487,488 | D69 | + - SH | 2 3 1 | 5 |
|  |  | B-4F1005 SH. 487,488 | D70 | + - SH | 2 3 1 | 6 |
|  |  | B-4F1005 SH. 487,488 | D71 | + - SH | 2 3 1 | 7 |
|  |  | B-4F1005 SH. 487,488 | D72 | + - SH | 2 3 1 | 8 |
| PF1B-PSS-2S CURRENT | pc_pf1b_pss_2s_i | B-4F1005 SH. 520,521 | D73 | + - SH | 2 3 1 | 9 |
| PF1B-PSS-1S CURRENT | pc_pf1b_pss_1s_i | B-4F1005 SH. 520,521 | D74 | + - SH | 2 3 1 | 10 |
| PF1B-PSS-2S VOLTAGE | pc_pf1b_pss_2s_v | B-4F1005 SH. 520,521 | D75 | + - SH | 2 3 1 | 11 |
| PF1B-PSS-1S VOLTAGE | pc_pf1b_pss_1s_v | B-4F1005 SH. 520,521 | D76 | + - SH | 2 3 1 | 12 |
| PF1AU-PSS-2S CURRENT | pc_pf1au_pss_2s_i | B-4F1005 SH. 522,523 | D77 | + - SH | 2 3 1 | 13 |
| PF1AU-PSS-1S CURRENT | pc_pf1au_pss_1s_i | B-4F1005 SH. 522,523 | D78 | + - SH | 2 3 1 | 14 |
| PF1AU-PSS-2S VOLTAGE | pc_pf1au_pss_2s_v | B-4F1005 SH. 522,523 | D79 | + - SH | 2 3 1 | 15 |
| PF1AU-PSS-1S VOLTAGE | pc_pf1au_pss_1s_v | B-4F1005 SH. 522,523 | D80 | + - SH | 2 3 1 | 16 |

| SLOT NO.: 17/19 | MODULE TYPE 908 TRANSIENT DIGITIZER, CHS 17-32 |
| --- | --- |

| SIGNAL NAME | DEVICE ID | CONT. DWG | CX | FCT | PIN# | CH |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | + - SH | 2 3 1 | 17 |
|  |  |  |  | + - SH | 2 3 1 | 18 |
|  |  |  |  | + - SH | 2 3 1 | 19 |
|  |  |  |  | + - SH | 2 3 1 | 20 |
|  |  |  |  | + - SH | 2 3 1 | 21 |
|  |  |  |  | + - SH | 2 3 1 | 22 |
|  |  |  |  | + - SH | 2 3 1 | 23 |
|  |  |  |  | + - SH | 2 3 1 | 24 |
|  |  |  |  | + - SH | 2 3 1 | 25 |
|  |  |  |  | + - SH | 2 3 1 | 26 |
|  |  |  |  | + - SH | 2 3 1 | 27 |
|  |  |  |  | + - SH | 2 3 1 | 28 |
|  |  |  |  | + - SH | 2 3 1 | 29 |
|  |  |  |  | + - SH | 2 3 1 | 30 |
|  |  |  |  | + - SH | 2 3 1 | 31 |
|  |  |  |  | + - SH | 2 3 1 | 32 |

| SLOT NO.: 17/19 | MODULE TYPE 908 TRANSIENT DIGITIZER, CLK/TRIG |
| --- | --- |

| SIGNAL NAME | CONT. DWG | FCT | PIN# |
| --- | --- | --- | --- |
| TRIGGER INPUT - UPPER | FROM 404A, CH 0 OF 7 N = 22 DEVICE : PCTM-1-1 | + - SH | 2 3 1 |
| TRIGGER INPUT - LOWER |  | + - SH | 2 3 1 |
| CLOCK INPUT - UPPER |  | + - SH | 2 3 1 |
| CLOCK INPUT - LOWER |  | + - SH | 2 3 1 |

| SLOT NO.: 20/21 | MODULE TYPE 404A TIMING MODULE |
| --- | --- |

| SIGNAL NAME | DEVICE ID | CONT. DWG | CROSS |  | CLR | PIN# | CH |
| --- | --- | --- | --- | --- | --- | --- | --- |
| CLEAN EARTH |  |  |  | F B | BRN TAN | 1B 1A | CE |
| START TRIGGER FOR CRATE 12 TRANSIENT DIGITIZER | PCTM-12-1 | 908, N=17 TRIG INPUT |  | F B | RED TAN | 2B 2A | 1 |
| CLEAN EARTH |  |  |  | F B | ORN TAN | 3B 3A | CE |
|  |  |  |  | F B | YLW TAN | 4B 4A | 2 |
| CLEAN EARTH |  |  |  | F B | GRN TAN | 5B 5A | CE |
|  |  |  |  | F B | BLU TAN | 6B 6A | 3 |
| CLEAN EARTH |  |  |  | F B | VIO TAN | 7B 7A | CE |
|  |  |  |  | F B | GRY TAN | 8B 8A | 4 |
| CLEAN EARTH |  |  |  | F B | BRN TAN | 9B 9A | CE |
|  |  |  |  | F B | RED TAN | 10B 10A | 5 |
| CLEAN EARTH |  |  |  | F B | ORN TAN | 11B 11A | CE |
|  |  |  |  | F B | YLW TAN | 12B 12A | 6 |
| CLEAN EARTH |  |  |  | F B | GRN TAN | 13B 13A | CE |
|  |  |  |  | F B | BLU TAN | 14B 14A | 7 |
| CLEAN EARTH |  |  |  | F B | VIO TAN | 15B 15A | CE |
|  |  |  |  | F B | GRY TAN | 16B 16A | 8 |

| SLOT NO.: 22 | MODULE TYPE 336 PC_LINK REPEATER |
| --- | --- |

| DESCRIPTION | CONMMENT | CONT'D DWG |
| --- | --- | --- |
| CONTROL FOR POWER SUPPLY : __EF4__________________________________ |
| HOUSE ADDRESS (HA) = E |  | N/A |
| SUBAGGREGATE HOUSE ADDRESS = _NONE . |  | N/A |
| PC LINK INPUT |  |  |
| PC LINK OUTPUT |  |  |
| I/O TO POWER SUPPLY CONTROLLER |  |  |