NSTX CALCULATION

Page 1 of 1

TITLE____PFC Heating/Cooling Thermal/Hydraulic Design

CALC. NO.____NSTX-CALC-11-07_____			DATE___6/30/98_____

ORIGINATOR___C Neumeyer________CHECKER____R Parsells___Rev.___0__

PURPOSE:

This calculation determines the flow, pressure drop, and temperature rise for the PFC heating/cooling circuits. It supercedes NSTX-CALC-11-05, "Thermal Analysis of NSTX Center Stack and Outboard Divertor Tiles", section "PFC Thermohydraulics". It also forms the basis for "Table 3.2-1: Dowtherm Thermal Hydraulic Requirements" in the PFC SDD NSTX-SDD-11-028.

REFERENCES:

1) Data sheet for "Dowtherm A" heat transfer fluid, attached.

2) "Flow of Fluids Through Valves, Fittings, and Pipe", Technical Paper No. 410, CRANE Engineering Division, 1979

ASSUMPTIONS:

1) Neglect pressure and temperature rise/drops through in-vessel manifolds which distribute the Dowtherm.

2) Assume friction factor ≈ constant over flow range considered (correct value used at nominal flow)

3) Neglect temperature rise/drop through the film resistance.

4) 12 Cooling paths* in each half plane, each cooling path 25' long, 0.5" OD, 0.049" wall tubing.

5) 70kW heating @ 350C, 100kW cooling @ 150C.

* Note: in the actual implementation, because of the lack of heated/cooled jumpers at the toroidal gaps of the passive plates, there is a cooling path on each side of the gap, so that the total number of paths is 13 in each half plane. However, for paths 12 and 13 the heating/cooling load sums to that of any one of the other paths, so for this calculation they are treated together as one.

CALCULATION:

See attached spreadsheets, with formulae and references given thereon. Two cases were run. In case 1 the fluid flows through the cooling paths with the upper and lower half planes in series (12 paths @ 25'). In case 2 the fluid flows throught the cooling paths with the upper and lower half planes in parallel (24 cooling paths @ 25'). Case 1 was the original design, case 2 is the final selected design.

CONCLUSION:

Design basis thermal hydraulic requirements are established by case 2.