Extension of Operation Range of NSTX to

Ip ≤ 1.5MA

C. Neumeyer

12/8/00

Issues related to increasing Ip up to 1.5MA:

- Availability of flux

- not addressed

- Ability of PF coil set to maintain equilibria

- addressed by scaling from 1.0MA cases

- Range of instrumentation

- addressed by R Marsala and J Menard

- EM forces during normal operation

- addressed

- EM forces during disruption

- addressed

- PF coil voltages during disruption

- addressed

Issues have been evaluated thus far without the benefit of a complete analysis (i.e. TSC, equilibria, SPARK and ANSYS) and without an exhaustive analysis of disruption behavior.

However, margins seem to be large, and no apparent show-stoppers have been identified.

Pending review of these findings it is recommended to:

- approve the higher level of operation at limited Bt (e.g. 4.5kG);

- resurrect the analysis work on SPARK and ANSYS;

- establish a disruption database;

- implement Digital Coil Protection system.

- Ability of PF coil set to maintain equilibria

• Scaled PF coil currents from original equilibria cases by 1.5, except for OH

• On this basis, 34 of 40 cases can be run within existing PF coil current limits

# Therefore it is assumed that no increase in PF coil current limits is required

| Config | 95 | 95 | li | Ipf1 | Ipf2 | Ipf3 | Ipf4 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 0 | 2 | 0.52 | 0 | 0.00 | 0.00 | 0.44 | 0.50 |  |
| ND | 1.99 | 0.52 | 0.2 | 0.13 | 0.00 | 0.57 | 0.48 |  |
| ND | 2 | 0.35 | 0.2 | 0.31 | 0.00 | 0.31 | 0.33 |  |
| ND | 2 | 0.35 | 0.2 | 0.51 | 0.00 | 0.43 | 0.32 |  |
| ND | 2 | 0.36 | 0.2 | 0.33 | 0.00 | 0.36 | 0.54 |  |
| ND | 2 | 0.36 | 0.2 | 0.53 | 0.00 | 0.47 | 0.53 |  |
| ND | 2 | 0.35 | 0.2 | 0.40 | 0.00 | 0.39 | 0.66 |  |
| ND | 2 | 0.35 | 0.2 | 0.60 | 0.00 | 0.49 | 0.66 |  |
| ND | 1.6 | 0.53 | 0.2 | 0.00 | 0.00 | 0.70 | 0.37 |  |
| ND | 1.6 | 0.53 | 0.2 | 0.21 | 0.00 | 0.80 | 0.37 |  |
| ND | 1.6 | 0.29 | 0.2 | 1.20 | 0.00 | 0.36 | 0.48 | X |
| ND | 1.6 | 0.33 | 0.2 | 1.20 | 0.00 | 0.56 | 0.47 | X |
| ND | 2 | 0.47 | 0.2 | -0.26 | 0.00 | 0.18 | 0.79 |  |
| ND | 2 | 0.49 | 0.6 | -0.13 | 0.00 | 0.31 | 0.76 |  |
| ND | 2 | 0.3 | 0.6 | 0.00 | 0.00 | 0.12 | 0.81 |  |
| ND | 2 | 0.3 | 0.6 | 0.26 | 0.00 | 0.23 | 0.80 |  |
| ND | 1.6 | 0.5 | 0.6 | -0.52 | 0.00 | 0.52 | 0.61 |  |
| ND | 1.6 | 0.5 | 0.6 | -0.31 | 0.00 | 0.62 | 0.61 |  |
| ND | 1.6 | 0.3 | 0.6 | 0.32 | 0.00 | 0.34 | 0.69 |  |
| ND | 1.6 | 0.3 | 0.6 | 0.59 | 0.00 | 0.42 | 0.69 |  |
| ND | 2.11 | 0.55 | 0.6 | 0.00 | -0.58 | 0.87 | 0.36 |  |
| DN | 2.11 | 0.53 | 0.2 | 0.17 | -0.38 | 0.83 | 0.41 |  |
| DN | 2.13 | 0.41 | 0.2 | 0.34 | -0.49 | 0.66 | 0.23 |  |
| DN | 2.13 | 0.39 | 0.2 | 0.55 | -0.32 | 0.65 | 0.26 |  |
| DN | 2.14 | 0.41 | 0.2 | 0.48 | -0.51 | 0.70 | 0.44 |  |
| DN | 2.14 | 0.39 | 0.2 | 0.69 | -0.35 | 0.69 | 0.47 |  |
| DN | 2.16 | 0.41 | 0.2 | 0.59 | -0.54 | 0.73 | 0.56 |  |
| DN | 2.15 | 0.39 | 0.2 | 0.80 | -0.38 | 0.73 | 0.58 |  |
| DN | 1.86 | 0.58 | 0.2 | 0.00 | -1.27 | 1.40 | 0.20 | X |
| DN | 1.86 | 0.59 | 0.2 | 0.13 | -1.11 | 1.41 | 0.22 | X |
| DN | 1.9 | 0.41 | 0.2 | 0.99 | -1.26 | 1.13 | 0.31 | X |
| DN | 1.9 | 0.41 | 0.2 | 1.14 | -1.11 | 1.14 | 0.33 | X |
| DN | 1.88 | 0.4 | 0.2 | -0.42 | -0.33 | 0.40 | 0.72 |  |
| DN | 1.92 | 0.38 | 0.6 | -0.24 | -0.13 | 0.36 | 0.76 |  |
| DN | 1.99 | 0.29 | 0.6 | 0.00 | -0.27 | 0.25 | 0.78 |  |
| DN | 2 | 0.27 | 0.6 | 0.24 | -0.13 | 0.26 | 0.80 |  |
| DN | 1.73 | 0.4 | 0.6 | -0.28 | -0.68 | 0.67 | 0.63 |  |
| DN | 1.74 | 0.4 | 0.6 | -0.15 | -0.53 | 0.69 | 0.64 |  |
| DN | 1.77 | 0.36 | 0.6 | 0.00 | -0.72 | 0.62 | 0.65 |  |
| DN | 1.77 | 0.36 | 0.6 | 0.15 | -0.57 | 0.64 | 0.67 |  |

## 2.0 Instrumentation Range

J Menard:

“A 1MA shot generates about 2V of integrator output, so we can probably double Ip before we run into any risk of saturating integrator/digitizer signals”

R Marsala:

“The change looks like a cinch. To change from 1.2 MA full scale to 2.0 MA full scale (2 MA suggested by Jon & Dave), I propose the following:

- Change A3R4 and A6R4 in the Ip&IPF1b Calculator Module from 10K to 6.04K.

- Re label test points on Ip&IPF1b Calculator Module.

- Adjust the two IPF1b input pots on the Ip Calculator Module to give 200KA/V

- instead of 120KA/V.

- Re label test points on Ip Calculator Module.

- Re label the Permissive Module test points from 120KA/V to 200kA/V.

- Change transfer functions on a few (6) TD channels.

- ECN  4 drawings.

- Software changes”

## 3.0 EM Forces During Normal Operation

### Plasma current generally decreases worst case force on coils, assuming that current directions are consistent with normal operations.

Relative Current Directions When Plasma Is Present

TF Coil Inner Legs – Primary concern is torsion on Inner Leg Bundle due to Jtf x Br which is due almost exclusively to Ioh and Ipf1a. In any case, since polarities of Ioh and Ip are opposite when Ip is large, Ip tends to reduce the torsion.

TF Coil Outer Legs – Primary concern is overturning moment due to Jtf x Bv which is due mainly to Ipf3 and Ipf5 and is generated on the top and bottom portions of the outer legs where Jtf is mostly radial. Since polarities of Ipf3 and Ipf5 are opposite to Ip,  the presence of Ip tends to reduce the force generated.

OH Coil – Primary concern is tensile stress in conductor due to Joh x Bz which is due almost exclusively to Ioh by itself. In any case since polarities of Ioh and Ip are opposite when Ip is large, Ip tends to reduce the field and force.

PFCoils – Axial and Radial Force Influence Matrices are used to assess mutual interactions. Using rated currents in nominal directions in OH, PF3, and PF5, and considering both polarities of PF1a and PF2, it is shown that the plasma decreases the force on the coil in nearly all cases and that stresses are well within allowables under all conditions.

PF Coil Axial Force Coefficients (FZ(j) = I(j)*∑Fz(i,j)*I(i))

|  | OH | PF1AU | PF1AL | PF1BL | PF2U | PF2L | PF3U | PF3L | PF4U | PF4L | PF5U | PF5L | PLA | PLB |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| OH | 0 | -9.6 | 9.6 | 53.3 | -54.1 | 54.1 | -27.7 | 27.7 | -4.6 | 4.6 | -5.9 | 5.9 | 0 | 0 |
| PF1AU | 9.6 | 0 | 0.05 | 0.05 | -24.2 | 0.26 | -2.55 | 0.96 | 3.06 | 1.56 | 3.51 | 2.2 | 0.13 | 0.09 |
| PF1AL | -9.6 | -0.05 | 0 | 97.2 | -0.26 | 24.2 | -0.96 | 2.52 | -1.56 | -3.06 | -2.2 | -3.51 | -0.13 | -0.09 |
| PF1BL | -53.3 | -0.05 | -97.2 | 0 | -0.29 | 17.9 | -1.1 | -7.16 | -1.84 | -4.87 | -2.72 | -5.81 | -0.11 | -0.07 |
| PF2U | 54.1 | 24.2 | 0.26 | 0.29 | 0 | 1.7 | 99.0 | 6.56 | 33.0 | 11.1 | 40.29 | 16.72 | 0.54 | 0.35 |
| PF2L | -54.1 | -0.26 | -24.2 | -17.9 | -1.7 | 0 | -6.6 | -99.0 | -11.08 | -33.0 | -16.7 | -40.3 | -0.54 | -0.35 |
| PF3U | 27.7 | 2.5 | 0.96 | 1.1 | -99.0 | 6.6 | 0 | 26.0 | 165.1 | 44.9 | 204.6 | 69.6 | 1.5 | 0.95 |
| PF3L | -27.7 | -0.96 | -2.5 | 7.2 | -6.6 | 99.0 | -26.0 | 0 | -44.9 | -165.1 | -69.6 | -204.6 | -1.5 | -0.95 |
| PF4U | 4.6 | -3.06 | 1.6 | 1.8 | -33.0 | 11.1 | -165.1 | 44.91 | 0.01 | 89.8 | 189.4 | 138.0 | 1.27 | 0.39 |
| PF4L | -4.6 | -1.6 | 3.1 | 4.9 | -11.1 | 33.0 | -44.9 | 165.1 | -89.8 | -0.01 | -138.0 | -189.4 | -1.27 | -0.39 |
| PF5U | 5.9 | -3.5 | 2.2 | 2.71 | -40.3 | 16.7 | -204.6 | 69.6 | -189.4 | 138.0 | 0 | 225.9 | 1.31 | 0.42 |
| PF5L | -5.9 | -2.2 | 3.5 | 5.81 | -16.7 | 40.3 | -69.6 | 204.6 | -138.0 | 189.4 | -225.9 | 0 | -1.31 | -0.42 |
| PLA | 0 | -0.13 | 0.13 | 0.11 | -0.54 | 0.54 | -1.5 | 1.5 | -1.27 | 1.27 | -1.31 | 1.31 | 0 | 0 |
| PLB | 0 | -0.09 | 0.09 | 0.07 | -0.35 | 0.35 | -0.95 | 0.95 | -0.39 | 0.39 | -0.42 | 0.42 | 0 | 0 |

PF Coil Radial (Hoop) Force Coefficients (FR(j) = I(j)*∑Fr(i,j)*I(i))

|  | OH | PF1AU | PF1AL | PF1BL | PF2U | PF2L | PF3U | PF3L | PF4U | PF4L | PF5U | PF5L | PLA | PLB |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| OH | 23112.1 | -33.8 | -33.8 | -57.7 | -18.9 | -18.9 | -15.2 | -15.2 | -10.5 | -10.5 | -14.1 | -14.1 | -0.4 | -0.2 |
| PF1AU | 2493.8 | 439.1 | 0.5 | 0.33 | -7.14 | 0.71 | -8.69 | 1.14 | -1.27 | 0.72 | -1.65 | 0.74 | 0.08 | 0.04 |
| PF1AL | 2493.8 | 0.5 | 439.1 | 22.7 | 0.71 | -7.14 | 1.14 | -8.69 | 0.72 | -1.27 | 0.74 | -1.65 | 0.08 | 0.04 |
| PF1BL | 1283.1 | 0.57 | 210.1 | 302.4 | 0.88 | -56.5 | 1.52 | -14.59 | 1.21 | -0.15 | 1.43 | -0.57 | 0.11 | 0.06 |
| PF2U | 942.3 | 180.4 | 3.41 | 2.44 | 387.2 | 5.5 | -110.4 | 9.7 | 4.1 | 8.4 | 1.5 | 10.3 | 0.67 | 0.4 |
| PF2L | 942.3 | 3.41 | 180.4 | 290.9 | 5.5 | 387.2 | 9.7 | -110.4 | 8.4 | 4.1 | 10.3 | 1.5 | 0.67 | 0.4 |
| PF3U | 1007.4 | 151.3 | 13.3 | 9.68 | 447.9 | 21.9 | 515.4 | 40.1 | 44.7 | 37.6 | 24.7 | 47.0 | 2.64 | 1.63 |
| PF3L | 1007.4 | 13.3 | 151.3 | 150.9 | 21.9 | 447.9 | 40.1 | 515.4 | 37.6 | 44.7 | 47.0 | 24.7 | 2.64 | 1.63 |
| PF4U | 667.4 | 53.8 | 20.9 | 14.9 | 92.4 | 33.3 | 166.1 | 59.0 | 184.4 | 56.8 | -899.0 | 57.5 | 4.28 | 2.48 |
| PF4L | 667.4 | 20.9 | 53.8 | 40.4 | 33.3 | 92.4 | 59.0 | 166.1 | 56.8 | 184.4 | 57.5 | -899.0 | 4.28 | 2.48 |
| PF5U | 903.8 | 70.7 | 32.3 | 23.7 | 130.0 | 54.0 | 264.1 | 100.2 | 1284.3 | 111.8 | 395.1 | 127.9 | 5.8 | 3.2 |
| PF5L | 903.8 | 32.3 | 70.7 | 55.0 | 54.0 | 130.0 | 100.2 | 264.1 | 111.8 | 1284.3 | 127.9 | 395.1 | 5.8 | 3.2 |
| PLA | 31.0 | 0.97 | 0.97 | 0.52 | 0.9 | 0.9 | 0.76 | 0.76 | -0.74 | -0.74 | -1.07 | -1.07 | 0.08 | 0.04 |
| PLB | 17.2 | 0.62 | 0.62 | 0.33 | 0.56 | 0.56 | 0.39 | 0.39 | -0.52 | -0.52 | -0.61 | -0.61 | 0.04 | 0.03 |

#### • Plasma Model

#### R (m)		Z (m)		Turn

#### PL-1U	0.85		0.80		0.066

#### PL-1L	0.85	       	-0.80		0.066

#### PL-4		1.20		0.00		0.225

#### PL-5		0.65		0.00		0.285

#### PL-2U	1.10		0.55		0.097

#### PL-2L	1.10	       	-0.55		0.097

#### PL-3U	0.65		0.55		0.082

#### PL-3L	0.65	       	-0.55		0.082

#### Total=  1.000

#### PLA-A represents the sum of PL-1U, PL-1L, PL-4, and PL-5.  The PLA-B represents the sum of PL-2U, PL-2L, PL-3U, and PL-3L.

#### Axial Forces For Four Cases

|  | Curr (kA) | EM Force w/o Plas (lb) | EM Force w/Plas (lb) | ¦∆¦% | Curr (kA) | EM Force w/o Plas (lb) | EM Force w/Plas (lb) | ¦∆¦% | Curr (kA) | EM Force w/o Plas (lb) | EM Force w/Plas (lb) | ¦∆¦% | Curr (kA) | EM Force w/o Plas (lb) | EM Force w/Plas (lb) | ¦∆¦% |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| OH | -24 | 25584 | 25584 | 0 | -24 | 25584 | 25584 | 0 | -24 | 25584 | 25584 | 0 | -24 | 25584 | 25584 | 0 |
| PF1AU | 15 | 11866 | 6916 | -42 | -15 | -11889 | -6939 | -42 | -15 | 2487 | 7437 | 199 | 15 | -2510 | -7460 | 197 |
| PF1AL | 15 | -41029 | -36079 | -12 | -15 | 41052 | 36102 | -12 | -15 | 26676 | 21726 | -19 | 15 | -26653 | -21703 | -19 |
| PF1BL | 20 | -10177 | -4777 | -53 | 20 | -68503 | -63103 | -8 | 20 | -54415 | -49015 | -10 | 20 | 3911 | 9311 | 138 |
| PF2U | 20 | 82883 | 56183 | -32 | 20 | 97571 | 70871 | -27 | -20 | -98931 | -72231 | -27 | -20 | -84243 | -57543 | -32 |
| PF2L | 20 | -75839 | -49139 | -35 | 20 | -90527 | -63827 | -29 | -20 | 91887 | 65187 | -29 | -20 | 77199 | 50499 | -35 |
| PF3U | -20 | -168849 | -95349 | -44 | -20 | -170937 | -97437 | -43 | -20 | -96961 | -23461 | -76 | -20 | -94873 | -21373 | -77 |
| PF3L | -20 | 172153 | 98653 | -43 | -20 | 174241 | 100741 | -42 | -20 | 100265 | 26765 | -73 | -20 | 98177 | 24677 | -75 |
| PF5U | -20 | -47906 | 3994 | -92 | -20 | -47120 | 4780 | -90 | -20 | -28264 | 23636 | -16 | -20 | -29050 | 22850 | -21 |
| PF5L | -20 | 51318 | -582 | -99 | -20 | 50532 | -1368 | -97 | -20 | 31676 | -20224 | -36 | -20 | 32462 | -19438 | -40 |
| PLU | 1500 |  |  |  | 1500 |  |  |  | 1500 |  |  |  | 1500 |  |  |  |
| PLL | 1500 |  |  |  | 1500 |  |  |  | 1500 |  |  |  | 1500 |  |  |  |

#### Stress Implication of Four Axial Force Cases

|  | Max* w/o Plas (lbs) | Max* w/Plas (lbs) | ¦∆¦% | SS CSA (in^2) | Max SS Stress (psi) |
| --- | --- | --- | --- | --- | --- |
| OH | 25584 | 25584 | 0 |  |  |
| PF1AU | 11889 | 7460 | -37 | 0.8 | 15852 |
| PF1AL | 41052 | 36102 | -12 | 0.8 | 54736 |
| PF1BL | 3911 | 9311 | 138 | 1.0 | 9311 |
| PF2U | 97571 | 70871 | -27 | 4.7 | 20705 |
| PF2L | 90527 | 63827 | -29 | 4.7 | 19210 |
| PF3U | -94873 | -21373 | -77 | 8.6 | -2474 |
| PF3L | 98177 | 24677 | -75 | 8.6 | 11364 |
| PF5U | -28264 | 23636 | -16 | 3.9 | 6019 |
| PF5L | 31676 | 20224 | -36 | 3.9 | 8066 |

* Maximum in direction in which force is weak, e.g. bolts or straps in tension (35ksi yield)

#### Radial Forces For Four Cases

|  | Curr (kA) | EM Force w/o Plas (lb) | EM Force w/Plas (lb) | ¦∆¦% | Curr (kA) | EM Force w/o Plas (lb) | EM Force w/Plas (lb) | ¦∆¦% | Curr (kA) | EM Force w/o Plas (lb) | EM Force w/Plas (lb) | ¦∆¦% | Curr (kA) | EM Force w/o Plas (lb) | EM Force w/Plas (lb) | ¦∆¦% |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| OH | -24 | 11831281 | 10096441 | -15 | -24 | 15422368 | 13687528 | -11 | -24 | 17231488 | 15496648 | -10 | -24 | 13640401 | 11905561 | -13 |
| PF1AU | 15 | 86121 | 121896 | 42 | -15 | 111690 | 75915 | -32 | -15 | 221970 | 186195 | -16 | 15 | -24159 | 11616 | -52 |
| PF1AL | 15 | 148986 | 184761 | 24 | -15 | 48825 | 13050 | -73 | -15 | 159105 | 123330 | -22 | 15 | 38706 | 74481 | 92 |
| PF1BL | 20 | 177169 | 202669 | 14 | 20 | 163381 | 188881 | 16 | 20 | -71323 | -45823 | -36 | 20 | -57535 | -32035 | -44 |
| PF2U | 20 | -97033 | -53233 | -45 | 20 | -93175 | -49375 | -47 | -20 | 407263 | 363463 | -11 | -20 | 411121 | 367321 | -11 |
| PF2L | 20 | -119997 | -76197 | -37 | 20 | -116139 | -72339 | -38 | -20 | 430227 | 386427 | -10 | -20 | 434085 | 390285 | -10 |
| PF3U | -20 | 402499 | 367999 | -9 | -20 | 397969 | 363469 | -9 | -20 | 317465 | 282965 | -11 | -20 | 321995 | 287495 | -11 |
| PF3L | -20 | 408943 | 374443 | -8 | -20 | 404413 | 369913 | -9 | -20 | 323909 | 289409 | -11 | -20 | 328439 | 293939 | -11 |
| PF5U | -20 | 226034 | 276434 | 22 | -20 | 225488 | 275888 | 22 | -20 | 234984 | 285384 | 21 | -20 | 235530 | 285930 | 21 |
| PF5L | -20 | 226834 | 277234 | 22 | -20 | 226288 | 276688 | 22 | -20 | 235784 | 286184 | 21 | -20 | 236330 | 286730 | 21 |

##### Stress Implication of Four Cases

|  | Max w/o Plas (lbs) | Max w/Plas (lbs) | ¦∆¦% | Cu CSA (in^2) | Max Avg Cu Stress (psi) |
| --- | --- | --- | --- | --- | --- |
| OH | 17231488 | 15496648 | -10 | 211.3 | 12979 |
| PF1AU | 221970.3 | 186195.3 | -16 | 24.9 | 1419 |
| PF1AL | 159105.3 | 184760.7 | 16 | 24.9 | 1181 |
| PF1BL | 177169.2 | 202669.2 | 14 | 14.5 | 2225 |
| PF2U | 411121 | 367321 | -11 | 25.4 | 2576 |
| PF2L | 434085 | 390285 | -10 | 25.4 | 2720 |
| PF3U | 402498.6 | 367998.6 | -9 | 27.2 | 2355 |
| PF3L | 408942.6 | 374442.6 | -8 | 27.2 | 2393 |
| PF5U | 235529.8 | 285929.8 | 21 | 22.2 | 2050 |
| PF5L | 236329.8 | 286729.8 | 21 | 22.2 | 2056 |

In summary, coil forces will not be increased during normal operations with the higher plasma current.

###### 4.0 EM Forces During Disruption

Toroidal current decay follows, to first order, the rate assumed by the design. Halo currents appear to be less than assumed (10% of Ip with toroidal peaking factor of 2).

Variations in the toroidal current decay rate effect the induced voltage on coupled structures (e.g. coils) but do not significantly effect the peak current induced in coupled structures whose time constant  >> decay time, i.e. dI ≈ ∫Vdt/L.

Original NSTX design was based on:

- 1.0 MA decay in 6.0mS

- toroidal jumpers between passive plates with saddle connection at one toroidal gap with resistance ≈ 100µΩ

- disruption calculations with all OH and PF open circuit ex

- 10% halo current flowing in poloidal direction with toroidal peaking factor of 2

- Bt ≤ 6kG

Analysis performed for the original design was as follows:

- SPARK was used to assess halo currents on center stack, based on 40% assumption (ref. NSTX-CALC-13-2, NSTX-CALC-13-13, 13-970214-JMS-01, “Center Stack Halo Current Stress Analysis”).  Because of “aspect ratio effect”, forces were found to be very low and not of concern.

- SPARK was used to assess the force on the center stack casing due to induced toroidal current  (ref. 13-970217-AWB-02, “Loads on CS from Plasma Disruption”), and the forces were found to be very low and not of concern.

- LRSIM and SPARK were used (and cross-checked) to determine induced voltages and currents in coils and structure based on axisymmetric and midplane symmetric model with 1.0MA/6mS ramp from plasma represented using one filament above and one filament below the midplane (ref. NSTX-CALC-11-1, 11-980514-CLN-01, “Disruption Calculations”).

- Forces on internal hardware (inner wall, passive plates, outboard divertor) from disruption were estimated (ref. NSTX-CALC-11-2, 11-980223-CLN-01, “Forces on Internal Hardware”) by taking the disruption currents, multiplying by a factor of 1.5 to account for non-centered plasma, and calculating J x B force based on worst case combination of PF coil currents to produce max Br and max Bz at each location.

Current Directions to Maximize Inward Forces

on Internal Hardware Components in the Lower Half Plane

|  |  | IW + |  | IBD + |  | OBD + |  | SPP + |  | PPP + |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Fv - | Fr + | Fv - | Fr + | Fv + | Fr - | Fv + | Fr - | Fv + | Fr - |
|  |  | Br + | Bv + | Br + | Bv + | Br - | Bv - | Br - | Bv - | Br- | Bv- |
| OH | -/0 | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 |
| PF1au | +/- | 0 | + | - | - | + | + | 0 | + | 0 | + |
| PF1al |  | + | + | - | - | + | + | - | + | - | + |
| PF1b | +/0 | + | + | + | + | 0 | + | 0 | + | 0 | + |
| PF2u | +/- | 0 | + | 0 | + | 0 | + | 0 | + | 0 | + |
| PF2l |  | + | + | + | + | - | + | - | + | - | + |
| PF3u | -/0 | - | 0 | - | 0 | 0 | - | 0 | - | 0 | - |
| PF3l |  | 0 | 0 | - | 0 | - | - | - | - | - | - |
| PF4 u&l | -/0 | - | 0 | - | 0 | 0 | - | 0 | - | 0 | - |
| SPP1u&l | +/0 | 0 | + | 0 | + | + | 0 | + | + | 0 | + |
| SPP2 u&l |  |  |  |  |  |  |  |  |  |  |  |
| PPP1 u&l |  |  |  |  |  |  |  |  |  |  |  |
| PPP2 u&l |  |  |  |  |  |  |  |  |  |  |  |
| Case |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 8 |
| ¦B¦max |  | 0.27 | 0.37 | 0.68 | 0.52 | 0.31 | 0.60 | 0.44 | 0.56 | 0.22 | 0.56 |

Table of Cases To Determine Worst Case Br and Bz Background Fields

- Forces and stresses on VV were analyzed by H.M. Fan via ANSYS using the forces from 4) above in combination with vacuum, normal EM, and dead load and found to be acceptable (ref. Report on "Vacuum Vessel Stress Analysis for NSTX Plasma Disruption Loads” by H.M. Fan).

- Forces and stresses on the Passive Plates and their support brackets were analyzed by ORNL (NSTX-CALC-11-06) using forces from 4) above and found to be significant but less than those associated with bakeout at 350oC which drove the design and the choice of CuCrZr alloy for the plates.

- Forces from 4) above on the outboard divertor back plates were used by G. Barnes in a NASTRAN finite element analysis of the “barbecue” mounting assembly (ref. NSTX-CALC-11-03) and found to result in acceptable levels of stress (peak EM stress of 4244 psi, peak thermal stress 3854 psi, not at same location) in the stainless steel rings.

- Worst case fields from 4) above were used by ORNL (ref. NSTX-CALC-11-04) as input to an analysis of the force on individual inner wall, inboard divertor, outboard divertor, and passive plate tiles due to halo currents as well as induced eddy currents from dB/dt due to 1.0 MA/1mS.

- Currents and forces in RF antenna faraday shield were calculated by P Bonanos (HHFW Antenna PDR) using worst case fields from any PF coil current combination along with induced current due to 1.0MA/6mS disruption (ref. 21-971211-CLN-01, “Planning for HHFW Antenna PDR”) and found to be benign (3.2kA, 2.9lb/in, 1.1ksi).

Disruption analysis has been updated using LRSIM for the following conditions:

- 1.5 MA decay in 9.0mS

- toroidal jumpers between passive plates with saddle connection at one toroidal gap with resistance 300µΩ on secondary and 400µΩ on primary

Under new conditions, current in passive plates is significantly reduced, while current in vacuum vessel is significantly increased.

LRSIM Filament Model

Peak Current Distribution in VV Filaments

With and Without Passive Plate Jumpers (1.0 MA  Disruption)

Taking worst case Br and Bz due to PF coils crossed with VV filament currents:

|  | Idis | Br | Bz | ¦B¦ | Fz | Fr | F | Pvv |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | (kA) | (T) | (T) | (T) | (lb) | (lb) | (lb) | (lb/in^2) |
| 1 | 9.6 | 0.060 | 0.30 | 0.306 | 1380.7 | 6903.4 | 7040.1 | 3.5 |
| 2 | 9.6 | 0.060 | 0.30 | 0.306 | 1380.7 | 6903.4 | 7040.1 | 3.5 |
| 3 | 9.4 | 0.090 | 0.30 | 0.313 | 2027.9 | 6759.5 | 7057.2 | 3.5 |
| 4 | 8.9 | 0.090 | 0.30 | 0.313 | 1920.0 | 6400.0 | 6681.8 | 3.3 |
| 5 | 8.2 | 0.140 | 0.56 | 0.577 | 2751.8 | 11007.0 | 11345.8 | 5.6 |
| 6 | 7.5 | 0.140 | 0.56 | 0.577 | 2516.8 | 10067.4 | 10377.2 | 5.1 |
| 7 | 6.9 | 0.220 | 0.56 | 0.602 | 3638.6 | 9262.0 | 9951.1 | 4.9 |
| 8 | 6.2 | 0.220 | 0.56 | 0.602 | 3269.5 | 8322.4 | 8941.6 | 4.4 |
| 9 | 5 | 0.220 | 0.56 | 0.602 | 2623.5 | 6678.0 | 7174.8 | 3.9 |
| 10 | 4.5 | 0.220 | 0.56 | 0.602 | 2314.7 | 5891.9 | 6330.3 | 3.5 |
| 11 | 4.3 | 0.220 | 0.30 | 0.372 | 2127.2 | 2900.7 | 3597.1 | 2.1 |
| 12 | 4.6 | 0.220 | 0.30 | 0.372 | 2146.0 | 2926.4 | 3628.9 | 1.9 |
| 13 | 4.6 | 0.340 | 0.30 | 0.453 | 3082.6 | 2720.0 | 4111.1 | 2.4 |
| 14 | 4.8 | 0.340 | 0.30 | 0.453 | 2964.5 | 2615.8 | 3953.6 | 2.5 |
| 15 | 4.8 | 0.310 | 0.60 | 0.675 | 2466.3 | 4773.5 | 5373.0 | 3.7 |
| 16 | 4.5 | 0.310 | 0.60 | 0.675 | 2084.6 | 4034.6 | 4541.3 | 3.4 |
| 17 | 3.9 | 0.310 | 0.30 | 0.431 | 1604.8 | 1553.1 | 2233.3 | 1.9 |
| 18 | 3.2 | 0.310 | 0.30 | 0.431 | 1147.9 | 1110.9 | 1597.5 | 1.6 |
| 19 | 2.5 | 0.310 | 0.20 | 0.369 | 762.7 | 492.1 | 907.6 | 1.0 |
| 20 | 1.8 | 0.310 | 0.30 | 0.431 | 451.2 | 436.6 | 627.8 | 0.9 |
| 21 | 0.9 | 0.200 | 0.30 | 0.361 | 113.6 | 170.4 | 204.7 | 0.4 |
| 22 | 0.4 | 0.200 | 0.20 | 0.283 | 36.1 | 36.1 | 51.1 | 0.1 |
| 23 | 0.1 | 0.200 | 0.20 | 0.283 | 5.4 | 5.4 | 7.7 | 0.0 |

With most of the current flowing in VV instead of plates, force on VV is more uniformly distributed than before, since reaction is directly from VV instead of discrete mounting points of passive plate supports. However, VV is closer to coils than plates, so field is somewhat higher.

Prior ANSYS work indicated the following non-additive peak stress in the VV:

Disruption (passive plate supports pulling inward):			18.2ksi

Normal EM loads (PF and TF coil supports) attached to VV:	11.4ksi

Vacuum:												10.9ksi

Dead weight load:										3.8ksi

New disruption load looks more like vacuum load, and the stress can be scaled from vacuum force approximately by:

(14.7 + 6)/14.7*10.9 ≈ 15ksi

Axial forces on PF coil supports are relatively small compared to forces from coil currents (even if they are summed they add to only 42.8kp).

Radial forces on PF coils are insignificant.

Peak current in OBD increases from 8.6kA to 15.4kA (at 1.0MA w/o jumpers) to 20.0kA (at 1.5MA w/o jumpers). Stress goes from 4.2ksi to 20/8.6*4.2 = 9.8ksi, still low.

Non-axisymmetric currents:

With passive plate jumpers removed, net non-axisymmetric currents flow in plates. Taking a crude plasma model (rectangular cross section) used by ORNL during the project design, the field B due to the plasma, normal to the plates, can be estimated, along with the initial value of the flux =B*A linked by a path around the periphery of the plate.

Then the current induced around the periphery of the plate can be estimated by ∆I=∆/L, where L is estimated via:

L = 0.004 * {a * ln(2a/) + b * ln(2b/) + 2 * sqrt(a^2+b^2) – a* arcsinh(a/b)-b*arcsinh(b/a)-2*(a+b)+µ/4*(a+b)}

Where:

a, b = sides of rectangular loop of conductor in cm

 = cross section of conductor = cm^2, assumed square conductor with width equal to thickness of plate

µ = 1

L = inductance in µH

(from Grover, p. 60, eq. 58)

#### Non-Axisymmetric Currents and Forces in Passive Plates

Forces of primary interest are those due to the poloidal current which form torsional couples and act in opposite directions on the supports at the ends of the plates.

|  | 1.0 MA |  | 1.5 MA |  |  |
| --- | --- | --- | --- | --- | --- |
|  | PPP | SPP | PPP | SPP |  |
| R1 | 53.540 | 43.823 | 53.540 | 43.823 | in |
| Z1 | 39.594 | 54.143 | 39.594 | 54.143 | in |
| R2 | 59.416 | 52.752 | 59.416 | 52.752 | in |
| Z2 | 21.775 | 41.509 | 21.775 | 41.509 | in |
| Lpoloidal | 18.763 | 15.471 | 18.763 | 15.471 | in |
| Theta | 71.749 | 54.749 | 71.749 | 54.749 | degrees |
| T | 0.500 | 0.500 | 0.500 | 0.500 | in |
| a | 75.112 | 64.220 | 75.112 | 64.220 | cm |
| b | 47.658 | 39.296 | 47.658 | 39.296 | cm |
| csa | 1.613 | 1.613 | 1.613 | 1.613 | cm^2 |
| L | 1.50668E-06 | 1.19654E-06 | 1.50668E-06 | 1.19654E-06 | H |
| Bnormal | 0.125 | 0.11 | 0.1875 | 0.165 | T |
| A | 0.358 | 0.252 | 0.358 | 0.252 | m^2 |
| Phi | 0.045 | 0.028 | 0.067 | 0.042 | weber |
| I | 29698.4 | 23199.5 | 44547.6 | 34799.3 | amp |
| Ravg | 1.435 | 1.227 | 1.435 | 1.227 | m |
| R0 | 0.854 | 0.854 | 0.854 | 0.854 | m |
| B(R0) | 0.600 | 0.600 | 0.600 | 0.600 | T |
| B(ravg) | 0.357 | 0.418 | 0.357 | 0.418 | T |
| Fn (I) | 1137 | 857 | 1706 | 1285 | lbs |
| Fz (I) | 356 | 494 | 534 | 742 | lbs |
| Fr (I) | 1080 | 700 | 1620 | 1049 | lbs |
| Ir | 9301 | 13390 | 13951 | 20085 | amp |
| Fz (Ir) | 356 | 494 | 534 | 742 | lbs |
| I (n=0) | 16100 | 6400 | 17700 | 7300 | amp |
| Br | 0.22 | 0.44 | 0.22 | 0.44 | T |
| Bz | 0.56 | 0.56 | 0.56 | 0.56 | T |
| Fr (I(n=0)) | 1522 | 517 | 1674 | 590 | lbs |
| Fz (I(n=0)) | 598 | 407 | 658 | 464 | lbs |
| ∑Fr | 2602 | 1217 | 3293 | 1639 | lbs |
| Fr (design) | 14160 | 5123 | 14160 | 5123 | lbs |
| Fr (% of design) | 18 | 24 | 23 | 32 | % |
| ∑Fz | 1310 | 1395 | 1726 | 1947 | lbs |
| Fz (design) | 5563 | 4025 | 5563 | 4025 | lbs |
| Fz (% of design) | 24 | 35 | 31 | 48 | % |

Forces are all less than the original design condition

Halo Currents:

If we reduce the assumed %Ip from 10% to 5%, and increase the plasma current from 1.0 to 1.5, then there is a net reduction to 5/10*1.5/1 = 75% of original design criteria. Such a reduction could also come in part from reduction in peaking factor.

| -->1MA<-- | Inner Wall | OBD | SPP | PPP |  |
| --- | --- | --- | --- | --- | --- |
| Ip | 1.00E+06 | 1.00E+06 | 1.00E+06 | 1.00E+06 | Amp |
| k | 0.10 | 0.10 | 0.10 | 0.10 |  |
| peaking | 2.00 | 2.00 | 2.00 | 2.00 |  |
| Ipoloidal | 8333.33 | 4166.67 | 16666.67 | 16666.67 | Amp |
| R0 | 0.854 | 0.854 | 0.854 | 0.854 | m |
| Bt(R0) | 0.600 | 0.600 | 0.600 | 0.600 | T |
| Bt(Ravg) | 2.694 | 0.561 | 0.436 | 0.378 | T |
| L poloidal | 0.152 | 0.624 | 0.292 | 0.582 | m |
| Fnormal/segment | 3421.39 | 1456.92 | 2118.99 | 3667.43 | N |
|  | 769.13 | 327.52 | 476.35 | 824.44 | lbs |
| Fradial/segment | 769.13 | 119.75 | 408.47 | 779.25 | lbs |
| Fvertical/segment | 0.00 | 304.84 | 245.08 | 269.20 | lbs |
| -->1.5 MA<-- |  |  |  |  |  |
| Ip | 1.50E+06 | 1.50E+06 | 1.50E+06 | 1.50E+06 | Amp |
| k | 0.05 | 0.05 | 0.05 | 0.05 |  |
| peaking | 2.00 | 2.00 | 2.00 | 2.00 |  |
| #segment | 24.00 | 48.00 | 12.00 | 12.00 |  |
| Ipoloidal | 6250.00 | 3125.00 | 12500.00 | 12500.00 | Amp |
| R0 | 0.854 | 0.854 | 0.854 | 0.854 | m |
| Bt(R0) | 0.600 | 0.600 | 0.600 | 0.600 | T |
| Bt(Ravg) | 2.694 | 0.561 | 0.436 | 0.378 | T |
| L poloidal | 0.152 | 0.624 | 0.292 | 0.582 | m |
| Fnormal/segment | 2566.04 | 1092.69 | 1589.24 | 2750.57 | N |
|  | 576.85 | 245.64 | 357.26 | 618.33 | lbs |
| Fradial/segment | 576.85 | 89.81 | 306.35 | 584.44 | lbs |
| Fvertical/segment | 0.00 | 228.63 | 183.81 | 201.90 | lbs |

5.0 PF Voltages During Disruption

For an open coil,  MdIp/dt will appear at the coil terminals. If coil is closed through its power supply in a conducting condition, then M*dIp/dt ≈ Lcoil*dIcoil/dt, i.e. ∆Icoil ≈ M∆Ip/L and little voltage change will be evident at coil terminals. However, if ∆Icoil is sufficient to drive the power supply current to zero in a unipolar circuit, then the MdIp/dt could appear.

If the plasma does not disrupt mid-plane symmetric, then different voltages will appear on upper and lower coils.

Maximum open circuit induced voltages are of order 1.8kV on OH and PF5 with midplane symmetry. Others are of order 1kV.

This should not be a problem because:

- OH and PF5 systems are very unlikely to be open circuited, if we have a 1.5 MA plasma.

- voltages are in any case ≤ 1/2 of those normally applied by the power supplies.

CONCLUSIONS

Issues have been evaluated thus far without the benefit of a complete analysis (i.e. TSC, equilibria, SPARK and ANSYS) and without an exhaustive analysis of disruption behavior.

However, margins seem to be large, and no apparent show-stoppers have been identified.

Pending review of these findings it is recommended to:

- approve the higher level of operation at limited Bt (e.g. 4.5kG);

- resurrect the analysis work on SPARK and ANSYS;

- establish a disruption database;

- implement Digital Coil Protection system.