NSTX CALCULATION

Page 1 of 1

TITLE____Electrical Demand and Cost Calculation

CALC. NO.____NSTX-CALC-51-01_____			DATE___3/3/99_____

ORIGINATOR___C Neumeyer________CHECKER____		__Rev.___0__

PURPOSE:

This calculation estimates the electrical demand of the NSTX facility and the associated costs.

REFERENCES:

1) "TFTR MG Sets Energy and Power Data", P Bonanos 10/28/94 (attached)

2) "Report of Test RT 257956, MG Flywheel Units", Canadian GE, Table 1.13

3) 1997/1998 Electricity Usage Data (attached)

4) e-mail from M Awad 2/26/99

ASSUMPTIONS:

1) Assume MG windage/friction/core losses per ref. 1) and 2)

2) Assume base D-site demand (peak and average) per ref. 3)

3) Neglect temperature rise/drop through the film resistance.

4) Assume billing structure per ref. 4)

5) Assume other misc. inputs as indicated on spreadsheet.

CALCULATION:

See attached spreadsheets, with formulae and references given thereon. Cells in border are data entry cells.

CONCLUSION:

If MG field is on all the time...

Cost per ops month ≈ $110k	Cost per maint month ≈ $60K

If field is off at all times except for the few seconds of the pulse...

Cost per ops month ≈ $95k