Simulation of OH Electrical Performance

C Neumeyer 4/11/97

General:

The program PSCAD/EMTDC is used to simulate the electrical performance of the OH coils and power supply system.

PSCAD presently resides on the EAD03 workstation. The files for the subject simulation have been downloaded and are stored on the NSTX file server along with this document.

PSCAD does not presently support the +/- 7.5 degree transformer phase shifting required for a 24-pulse rectifier system. Therefore this feature is excluded, and the maximum pulse number is 12. This does not effect the results and conclusions however. Only the harmonic content will differ.

The assumed power supply configuration consists of four series layers (six is an option, but the system should work with four), and two anti parallel Transrex power supply sections. Each pair of sections are contained in one power supply unit which is assumed the only load on the associated feeder. This is the configuration expected in the field.

Main circuit is shown on simulation drawing subsystem 1 of 4. All resistances and inductances on the secondary side of the converter transformer, including the DC side, are scaled up by 10^2 = 100 in order to permit the entry of the low values required. At the same time the voltage is scaled up by 10.  Reported results are rescaled appropriately.

Only one parallel is simulated. When the current reaches zero and should cross over, instead it resumes in the same direction. This simulation approach is entirely valid for the purposes of the investigations described herein; the coil behavior and power supply voltage drop issues are identical.

MG Model:

The MG is designed to regulate the SV bus voltages by feedback control of the excitation. So, to the extent that the feedback can respond to changes in load, the voltage will be constant. The response time is finite however, and the loads change rather quickly.

In real operation the MG load is the composite of all systems. In the simulation, only the TF system loads it. On the other hand the feed back control is not included, but the stator self inductance and resistance is included. So there is some regulation of the MG bus voltage, but it is not

accurately represented in detail for the reasons cited. However, the effect is small and not really significant.

Derivation of MG electrical model parameters is as follows....

| Generator Xs | 0.0665 | Ω/ph @ 60Hz |
| --- | --- | --- |

| Generator CLR X | 0.0140 | Ω/ph @ 60Hz |
| --- | --- | --- |

| Generator Ls | 1.76E-04 | h/phase |
| --- | --- | --- |

| Generator CLR L | 3.71E-05 | h/phase |
| --- | --- | --- |

| ∑ L | 2.14E-04 |  |
| --- | --- | --- |

| Generator Rs | 1.20E-03 | Ω/phase |
| --- | --- | --- |

| Generator CLR R | 2.00E-04 | Ω/phase |
| --- | --- | --- |

| ∑ R | 1.40E-03 | Ω/phase |
| --- | --- | --- |

| Feeder CLR X | 0.5 | Ω/ph @ 60Hz |
| --- | --- | --- |

The mechanical energy storage effects and windage, friction, eddy loss effects of the MG are modeled using the system shown on the simulation subsystem drawing sheet 2 of 4.

Motor stator power input was set to zero for the simulations. The net mechanical input power to the system is...

Pin = Pstator * f/fsynch

where Pin is the net power in,  Pstator is the motor stator input power, f is the frequency of the MG output voltage, and fsynch is 76.36Hz, which is the frequency of the MG output voltage corresponding to motor synchronous speed.

Power lost to the TF coil is taken out of the MG stored energy as the simulation progresses through the Ptf term.

Power losses due to windage, friction, and eddy/hysteresis losses are based on the following...

Ploss = Kw * f^3 + Kf * f^1.2 + Keh * f

where 	Ploss = power loss in watts

f = generator output frequency in Hz

(=87.5Hz at 375 rpm)

Kw = windage coefficient = 3.341

Kf = friction coefficient = 2.376 x 103

Keh = eddy & hysteresis coefficient = 1.576 x 104

Inertia constant and initial stored energy corresponing to 70Hz are derived as follows using

∆W = Kinertia*(f0^2-f^2)

and accounting for the fact that 2.25GJ is delivered during spin down from 87.5 to 60Hz....

| Delivered Energy | 2.25E+09 |
| --- | --- |

| Max Speed | 87.5 |
| --- | --- |

| Min Speed | 60 |
| --- | --- |

| Inertia Constant | 554699.5378 |
| --- | --- |

| Nominal Speed | 70 |
| --- | --- |

| Nominal Stored Energy | 2.7180E+09 |
| --- | --- |

| Max Stored Energy | 4.25E+09 |
| --- | --- |

The use of 70Hz as an initial speed is conservative.

As shown in the following table, the amount of energy needed by NSTX in total (<< 170MJ as noted in the WBS5 SRD) would allow lower starting speeds.

| Wdelivered | 2.25E+09 |  |
| --- | --- | --- |

| f1 | 87.5 |  |
| --- | --- | --- |

| f0 | 60 |  |
| --- | --- | --- |

| K | 554699.5378 |  |
| --- | --- | --- |

| Wstored @ |  | Wreleased to 60Hz |
| --- | --- | --- |

| 90 | 4493.07 | 2496.15 |
| --- | --- | --- |

| 89 | 4393.78 | 2396.86 |
| --- | --- | --- |

| 88 | 4295.59 | 2298.67 |
| --- | --- | --- |

| 87 | 4198.52 | 2201.60 |
| --- | --- | --- |

| 86 | 4102.56 | 2105.64 |
| --- | --- | --- |

| 85 | 4007.70 | 2010.79 |
| --- | --- | --- |

| 84 | 3913.96 | 1917.04 |
| --- | --- | --- |

| 83 | 3821.33 | 1824.41 |
| --- | --- | --- |

| 82 | 3729.80 | 1732.88 |
| --- | --- | --- |

| 81 | 3639.38 | 1642.47 |
| --- | --- | --- |

| 80 | 3550.08 | 1553.16 |
| --- | --- | --- |

| 79 | 3461.88 | 1464.96 |
| --- | --- | --- |

| 78 | 3374.79 | 1377.87 |
| --- | --- | --- |

| 77 | 3288.81 | 1291.90 |
| --- | --- | --- |

| 76 | 3203.94 | 1207.03 |
| --- | --- | --- |

| 75 | 3120.18 | 1123.27 |
| --- | --- | --- |

| 74 | 3037.53 | 1040.62 |
| --- | --- | --- |

| 73 | 2955.99 | 959.08 |
| --- | --- | --- |

| 72 | 2875.56 | 878.64 |
| --- | --- | --- |

| 71 | 2796.24 | 799.32 |
| --- | --- | --- |

| 70 | 2718.03 | 721.11 |
| --- | --- | --- |

| 69 | 2640.92 | 644.01 |
| --- | --- | --- |

| 68 | 2564.93 | 568.01 |
| --- | --- | --- |

| 67 | 2490.05 | 493.13 |
| --- | --- | --- |

| 66 | 2416.27 | 419.35 |
| --- | --- | --- |

| 65 | 2343.61 | 346.69 |
| --- | --- | --- |

| 64 | 2272.05 | 275.13 |
| --- | --- | --- |

| 63 | 2201.60 | 204.68 |
| --- | --- | --- |

| 62 | 2132.27 | 135.35 |
| --- | --- | --- |

| 61 | 2064.04 | 67.12 |
| --- | --- | --- |

| 60 | 1996.92 | 0.00 |
| --- | --- | --- |

Since the heating of the cycloconverter increases as the MG speed deviates from 76.26Hz, a comfortable minimum idling speed is ≈ 65Hz. Since the power supply regulation gets worse as the speed increases, the 70Hz initial condition is chosen as a conservative value.

Feeder (SV bus to transformer primary):

Feeder impedances are as follows....

| 2p 500MCM 70' X | 0.00168 | Ω/ph @ 60Hz | NEC Table 9 0.048Ω/1000' for 500MCM in steel conduit |
| --- | --- | --- | --- |

| Feeder CLR L | 0.00132626 | h/phase |  |
| --- | --- | --- | --- |

| 2p 500MCM 70' L | 4.45623E-06 | h/phase |  |
| --- | --- | --- | --- |

| ∑ L | 1.33E-03 | h/phase |  |
| --- | --- | --- | --- |

| Feeder CLR X/R | 44 |  |  |
| --- | --- | --- | --- |

| Feeder CLR R | 0.011363636 | Ω/phase |  |
| --- | --- | --- | --- |

| 2p 500MCM 70' R | 0.001015 | Ω/phase | NEC Table 9 0.029Ω/1000' for 500MCM in steel conduit |
| --- | --- | --- | --- |

| ∑ R | 1.24E-02 | Ω/phase |  |
| --- | --- | --- | --- |

| 1p 500MCM 435' X | 0.02088 | Ω/ph @ 60Hz | NEC Table 9 0.048Ω/1000' for 500MCM in steel conduit |
| --- | --- | --- | --- |

| 1p 500MCM 435' L | 5.53846E-05 | h/phase |  |
| --- | --- | --- | --- |

| 1p 500MCM 435' R | 0.012615 | Ω/phase | NEC Table 9 0.029Ω/1000' for 500MCM in steel conduit |
| --- | --- | --- | --- |

The above accounts for two parallel 500MCM cables/phase, length 70', from the CLR to the switchgear, and one cable/phase, length 435', from the switchgear to the transformer.

Transformer:

See attached spreadsheet and transformer test data sheets. The final derived numbers are.....

| Rh | 0.060666667 | Ω |
| --- | --- | --- |

| Xh | -6.6003 | %@25MVA |
| --- | --- | --- |

| Lh | -0.001333686 | henries |
| --- | --- | --- |

| Rs | 0.000363 | Ω |
| --- | --- | --- |

| Xs | 37.1322 | %@25MVA |
| --- | --- | --- |

| Ls | 2.21616E-05 | henries |
| --- | --- | --- |

| Imag | 0.878378378 | %@25MVA,1.0 p.u.Voltage |
| --- | --- | --- |

| Xh-s | 30.5318 | %@25MVA |
| --- | --- | --- |

| Xs-s | 74.26435701 | %@25MVA |
| --- | --- | --- |

DC Connections:

Cable length estimates are given on the attached spreadsheet "NSTX Loop Resistances".

Summary is as follows.....

| PSS/SDS R | 2.50E-03 | Ω |
| --- | --- | --- |

| SDS/Waterfall R | 5.43E-04 | Ω |
| --- | --- | --- |

| ∑ R | 3.04E-03 | Ω |
| --- | --- | --- |

| Waterfall/Hot Cell R | 5.00E-03 | Ω |
| --- | --- | --- |

| Total Effective R | 8.04E-03 | Ω |
| --- | --- | --- |

Coil Impedance:

Variation of resistance with temperature is accomplished using the functions shown on simulation drawing subsystem 3 of 4. These are based on the "G" function of copper, and the conductor cross sectional area (refer to NSTX Calc 13-2-0 "PF Coil Parameters" for a description).  To effect the change in resistance, an artificial current source is placed across the initial resistance of the coil in order to produce a voltage drop equal to that attributable to actual resistance of the coil as it heats up.

Calculations are based on an initial coil temperature of 10C.

Inductance of the coil is taken from NSTX Calc 13-2-0 "PF Coil Parameters".

Mutual coupling to other coil circuits is neglected.

Results:

The worst case ∫i^2(t)dt inductive scenario (scenario II, with 0.4 sec plasma ramp rate and 0.5 second plasma flat top) was chosen (ref. 72-970129-SMK-01).

The ∫i^2(t)dt from the simulation is equal to 2.3e9 amp^2-sec. The corresponding ESW at the rated current of 24kA is 0.4 seconds, which is well below the coil rating of 3e8 amp^2-sec and ESW of 0.52 seconds.

Using the 4kV power supply, the volts per turn during initiation is ≥ 4 volts, but the current derivative is 333 kA/sec compared to the desired value of 410 kA/sec. To achieve the higher derivative if required the 6kV power supply will more than suffice (6/4 = 1.5 > 410/333 = 1.23).