FIRE SITE POWER ISSUES

C Neumeyer 11/24/99

• FIRE Power Demand compared to ITER

FIRE
Pmax (+)
Wmax


PF
114
2.25
JHS 6/9/99 

TF
500.4
11.2
RDW 9/14/99

Heating
60
1.2
30 MW @ 0.5 eff

∑
674.4
14.65


BOP
?



ITER




PF
225



TF
35



Heating
300



∑
560
50.4


BOP
250



· peak power is similar (≈ ITER bogey of 600MW)

· energy is much less

· BOP is much less if refrigeration plant not at site

• Implications

· feasible to supply power from grid 

· V≈500kV

· Short Circuit Power  >10GVA

· feasible to supply power from mix 

· grid @ V less than 500kV

· powerful MG system

· e.g. if PPPL can take 325MW from 138kV for 30 seconds, load remaining on MG would be ≈ TFTR MG capabilities


Pmax (+)
Wmax

∑ - 325MW/30s
349.4
4.9

• Taking power from the grid

· many complex issues, both technical, commercial, and political

· pulsed load is not commercially attractive to utility

· it must provide the capability of generating and transmitting the power but does not get any energy revenue

· duration is too short to significantly effect the demand metering

· deregulated market makes pulsed load even less attractive

- recommend early interaction with prospective host utilities, at both technical and political levels

• Comments on proposed sites

· In order to supply the power

· a high density of HV lines (345, 500, and 765) kV is desirable to ensure high short circuit power

· close proximity of an HV line is desirable to deliver the power, and or low population density to allow the construction of a new power line

· availability of a large MG set(s) would relieve the grid power requirement

· Amongst the sites proposed, those in New Mexico seem to be the least attractive from point of view of available grid power

· The others are situated better, but may not have direct access via a HV line

· PPPL benefits from its MG sets

