August 14, 2000

TO: R SIMMONS

FROM: C NEUMEYER

SUBJECT: FIRE POWER SYSTEM COST ESTIMATE, REVISED

References:

# [1] R. Woolley, FIRE Interim Engineering Report, Sec. 5.13, 9/14/99 Update

[2] Technical & Cost Assessment of the PCAST Machine, Final Report, 12/95

[3] ITER DDD. Coil Power Supply & Distribution (WBS 4.1), Issue 3,: June 2, 1995

[4] ITER Cost Assessment Document, Coil Power Supply & Distribution (WBS 4.1), Issue 1: 19 April 1995.

[5] “Guidance for Developing the FIRE Pre-Conceptual Estimate”, R Simmons, 8/6/99

This memo presents a pre-conceptual top-down cost estimate of the FIRE Power Systems (WBS 4). Power requirements are based on [1]. The costing method is the same as that used for PCAST [2], which is based on adjustments to the ITER cost data [3,4].

[6] “FIRE Power Systems Cost Estimate”, C. Neumeyer, 6/5/2000

This memo is an update of reference [6] with corrections in the tabulated cost summary.

# Power Requirement

The following assumptions are made with respect the power requirement, and the energy and duty cycle:

## • TF (Vno-load * Ipeak)

### - 541.5 MVA(unipolar, 2 quadrant) as required for 10 Tesla

## • PF (∑Vno-load * Ipeak, non-coincident)

### -120.4 MVA (unipolar, 2 quadrant)

### - 291.6 MVA (bipolar, 4 quadrant)

## • Auxiliary Heating

### -75 MVA (assumed 30MW ICRF, 50% eff, 0.8 p.f.)

## • Internal Control Coils

### - 2*75 volt/turn*75kA-turn = 11.2 MW (per C. Kessel e-mail)

### • Internal Control Coils

### - 2*75 volt/turn*75kA-turn = 11.2 MW (per C. Kessel e-mail)

## • Field Error Correction Coils

- 1MVA (guesstimate)

### • Resistive Wall Mode Coils

- 5MVA (same as GA DIII-D)

## • Energy requirement (peak delivered)

### -TF 11.2 GJ

### -PF 2.1 GJ

### -Auxiliary Heating 30/.5*20= 1.2 GJ

## • Plasma flat top ~20 sec

## • Repetition period 3 hours

# Scaling from ITER Data

## Original ITER costs from EU Home Team industrial estimates in 1995

## Conversion from 1995 ECU to USD ≈ 1.3 USD/ECU

## Conversion from 1995 to 1999 = 1.117 per R. Simmons

## ITER Costs include….

## manufacturing (detailed design, fabrication, factory testing)

## local control & protection

## installation, site commissioning, documentation & QA

## recommended spares, and transportation costs

• ITER Costs do not include…

- project system engineering/integration

- contingency

# Adjustments from ITER Data based on Duty Cycle

• Cables, Bus Bar, Switches, DC inductors - a 50% reduction from the ITER requirement is assumed. The conductor cross sections would be reduced beyond this amount but the costs associated with bracing for fault conditions remains the same as for ITER.

• Transformers - no reduction was taken since the impedance must not be increased (e.g. the MVA rating cannot be decreased) and since the bracing for fault conditions remains the same as for ITER. In practice it is expected that the converter transformers would be less costly, however, since their high current secondary windings would be simplified.

• Thyristors - no reduction was taken since the water-cooled thyristors reach thermal equilibrium within the time interval of the pulse.

• Switchgear - no reduction was taken since the fault interrupting rating, which is the primary cost driver, remains the same as for ITER.

The above reductions were taken on the hardware portion of the costs where appropriate; the other cost categories (e.g. design, commissioning, etc. were not adjusted).

# Other Assumptions & Adjustments

• Total installed capacity of PF power supply system was taken as…

1.5 * ∑iVno-loadi*Ipeaki

…to account for inefficiency in supplying the 7 PF systems (each with unique ratings) by a few (maybe 2 or 3) AC/DC converter ratings.

• Substation/Utility Interface MVA rating was assumed to be 1/2 that of ITER

-FIRE installed AC/DC converter power level is somewhat less than 1/2 of ITER, but power supplies would be used more efficiently on FIRE than on ITER since a much larger fraction of the FIRE power supply is used for TF, which is not subject to dynamic load swings

• Assumed same factor as ITER for ratio of Reactive Power Compensation to rating of Substation/Utility Interface

• Considered variant with 1/2 rated Substation/Utility Interface and remaining power supplied by MG, based on the use of 2 TFTR MG sets, and associated cost escalated to present.

• Assumed same cost as ITER for DC Circuit Breaker/Blip Resistors for Plasma Initiation

- same number of circuits

- ampacity requirements less on FIRE, but this reduction is neglected for now

• Assumed 60MVA Auxiliary Power System (same as PPPL D-site utility interface; this needs further definition)

Summary of Costs

The following two tables give the cost summary. The first table corresponds to the case where the local utility grid supplies all of the power, the second where it is supplemented by a Motor-Generator (MG) energy storage system of the same size as the TFTR system, consisting of two units at 475MVA, 2.25GJ each. Contingency calculation is based on instructions given in [5].

FIRE POWER SYSTEM COSTS
(all power supplied directly from grid)

| CATEGORY | FIRE Rating (MVA) | ITER Scaling ($95/ MVA) | Fire Cost (M$99) | TR | TW | SR | SW | CR | CW | Cont | C$ |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Utility Grid Interface | 600.0 | 4.6 | 3.1 | 1 | 2 | 8 | 1 | 1 | 2 | 12 | 0.4 |
| Substation | 600.0 | 15.1 | 10.1 | 1 | 2 | 8 | 1 | 1 | 2 | 12 | 1.2 |
| Energy Storage System | 0.0 |  | 0.0 | 2 | 2 | 8 | 1 | 4 | 2 | 20 | 0.0 |
| Reactive Power Compensation | 300.0 | 29.2 | 9.8 | 2 | 2 | 8 | 1 | 4 | 2 | 20 | 2.0 |
| ∑AC Distribution | 1545.8 | 3.0 | 5.2 | 1 | 2 | 8 | 1 | 1 | 2 | 12 | 0.6 |
| AC/DC Converters | 1170.8 |  |  |  |  |  |  |  |  |  |  |
| Auxiliary Heating | 75.0 |  |  |  |  |  |  |  |  |  |  |
| Reactive Compensation | 300.0 |  |  |  |  |  |  |  |  |  |  |
| TF AC/DC Converters | 541.5 | 49.8 | 30.1 | 4 | 2 | 8 | 1 | 4 | 2 | 24 | 7.2 |
| ∑PF AC/DC Converters | 618.0 |  | 37.5 | 4 | 2 | 8 | 1 | 4 | 2 | 24 | 9.0 |
| -PCAST/FIRE* 4Q AC/DC PF | 437.4 | 56.2 | 27.5 |  |  |  |  |  |  |  |  |
| -FIRE* 2Q AC/DC PF | 180.6 | 49.8 | 10.0 |  |  |  |  |  |  |  |  |
| PF Switching Networks |  |  | 32.3 | 6 | 2 | 8 | 1 | 6 | 2 | 32 | 10.3 |
| -Switching Network Units |  |  | 32.3 |  |  |  |  |  |  |  |  |
| Fast Plasma Position Control PS | 11.3 | 175.6 | 2.2 | 6 | 2 | 4 | 1 | 6 | 2 | 28 | 0.6 |
| Field Error Correction PS | 1.0 | 100.0 | 0.1 | 2 | 2 | 4 | 1 | 6 | 2 | 20 | 0.0 |
| Resistive Wall Mode PS | 10.0 | 175.6 | 2.0 | 3 | 2 | 4 | 1 | 6 | 2 | 22 | 0.4 |
| Instrumentation |  |  | 2.7 | 6 | 2 | 8 | 1 | 4 | 2 | 28 | 0.8 |
| DC Components & Dummy Loads |  |  | 16.9 | 4 | 2 | 4 | 1 | 4 | 2 | 20 | 3.4 |
| Exp Power System Engineering |  |  | 11.5 |  |  |  |  |  |  |  |  |
| TOTAL EXP PWR SYS (4.2) |  |  | 163.4 |  |  |  |  |  |  | 22 | 35.9 |
| Auxiliary Power System | 60.0 | 120.8 | 8.1 |  |  |  |  |  |  |  |  |
| Aux Power System Engineering |  |  | 5.8 |  |  |  |  |  |  |  |  |
| TOTAL AUX POWER SYSTEM (4.1) |  |  | 13.9 | 1 | 2 | 8 | 1 | 4 | 2 | 18 | 2.5 |
| GRAND TOTAL |  |  | 177.3 |  |  |  |  |  |  |  | 38.4 |

FIRE POWER SYSTEM COSTS
(w/Supplemental MG Energy Storage)

| CATEGORY | FIRE Rating (MVA) | ITER Scaling ($95/ MVA) | Fire Cost (M$99) | TR | TW | SR | SW | CR | CW | Cont | C$ |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Utility Grid Interface | 300.0 | 4.6 | 1.5 | 1 | 2 | 8 | 1 | 1 | 2 | 12 | 0.2 |
| Substation | 300.0 | 15.1 | 5.1 | 1 | 2 | 8 | 1 | 1 | 2 | 12 | 0.6 |
| Energy Storage System | 950.0 |  | 44.8 | 2 | 2 | 8 | 1 | 4 | 2 | 20 | 9.0 |
| Reactive Power Compensation | 150.0 | 29.2 | 4.9 | 2 | 2 | 8 | 1 | 4 | 2 | 20 | 1.0 |
| ∑AC Distribution | 1545.8 | 3.0 | 5.2 | 1 | 2 | 8 | 1 | 1 | 2 | 12 | 0.6 |
| AC/DC Converters | 1170.8 |  |  |  |  |  |  |  |  |  |  |
| Auxiliary Heating | 75.0 |  |  |  |  |  |  |  |  |  |  |
| Reactive Compensation | 300.0 |  |  |  |  |  |  |  |  |  |  |
| TF AC/DC Converters | 541.5 | 49.8 | 30.1 | 4 | 2 | 8 | 1 | 4 | 2 | 24 | 7.2 |
| ∑PF AC/DC Converters | 618.0 |  | 37.5 | 4 | 2 | 8 | 1 | 4 | 2 | 24 | 9.0 |
| -PCAST/FIRE* 4Q AC/DC PF | 437.4 | 56.2 | 27.5 |  |  |  |  |  |  |  |  |
| -FIRE* 2Q AC/DC PF | 180.6 | 49.8 | 10.0 |  |  |  |  |  |  |  |  |
| PF Switching Networks |  |  | 32.3 | 6 | 2 | 8 | 1 | 6 | 2 | 32 | 10.3 |
| -Switching Network Units |  |  | 32.3 |  |  |  |  |  |  |  |  |
| Fast Plasma Position Control PS | 11.3 | 175.6 | 2.2 | 6 | 2 | 4 | 1 | 6 | 2 | 28 | 0.6 |
| Field Error Correction PS | 1.0 | 100.0 | 0.1 | 2 | 2 | 4 | 1 | 6 | 2 | 20 | 0.0 |
| Resistive Wall Mode PS | 10.0 | 175.6 | 2.0 | 3 | 2 | 4 | 1 | 6 | 2 | 22 | 0.4 |
| Instrumentation |  |  | 2.7 | 6 | 2 | 8 | 1 | 4 | 2 | 28 | 0.8 |
| DC Components & Dummy Loads |  |  | 16.9 | 4 | 2 | 4 | 1 | 4 | 2 | 20 | 3.4 |
| Exp Power System Engineering |  |  | 11.5 |  |  |  |  |  |  |  |  |
| TOTAL EXP PWR SYS (4.2) |  |  | 196.7 |  |  |  |  |  |  | 22 | 43.1 |
| Auxiliary Power System | 60.0 | 120.8 | 8.1 |  |  |  |  |  |  |  |  |
| Aux Power System Engineering |  |  | 5.8 |  |  |  |  |  |  |  |  |
| TOTAL AUX POWER SYSTEM (4.1) |  |  | 13.9 | 1 | 2 | 8 | 1 | 4 | 2 | 18 | 2.5 |
| GRAND TOTAL |  |  | 210.6 |  |  |  |  |  |  |  | 45.6 |

Schedule

Following is a tentative schedule for the power systems, assuming a 9 year program leading to first plasma [5].

| Task/Year | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| WBS 4.1 (Aux PS) |  |  |  |  |  |  |  |  |  |  |
| Conceptual Design |  |  |  |  |  |  |  |  |  |  |
| Preliminary Design |  |  |  |  |  |  |  |  |  |  |
| Fabrication |  |  |  |  |  |  |  |  |  |  |
| Final Design |  |  |  |  |  |  |  |  |  |  |
| Installation |  |  |  |  |  |  |  |  |  |  |
| Commissioning |  |  |  |  |  |  |  |  |  |  |
| Aux Sys Engr | 1 | 1 | 2 | 4 | 4 | 4 | 4 | 2 | 2 | 24 |
| WBS 4.2 (EXP PS) |  |  |  |  |  |  |  |  |  |  |
| Conceptual Design |  |  |  |  |  |  |  |  |  |  |
| Preliminary Design |  |  |  |  |  |  |  |  |  |  |
| Fabrication |  |  |  |  |  |  |  |  |  |  |
| Final Design |  |  |  |  |  |  |  |  |  |  |
| Installation |  |  |  |  |  |  |  |  |  |  |
| Commissioning |  |  |  |  |  |  |  |  |  |  |
| Exp Sys Engr | 2 | 2 | 4 | 6 | 8 | 8 | 6 | 6 | 6 | 48 |

cc:

P Heitzenroeder

R Woolley