5/24/2

# TO: R SIMMONS,  D MEADE

FROM: C NEUMEYER

SUBJECT: REVISED COST ESTIMATE FOR FIRE POWER SYSTEMS

Reference:

“FIRE Power System Cost Estimate, Revised”, C Neumeyer to R Simmons, 8/14/2000

This memo presents a revised cost estimate for the power systems, which is consistent with the information being supplied to the Snowmass Meeting. In terms of $2002, it is around 16% lower than the prior estimate.

The major changes are as follows:

- Costs inflated to 2002 using Snowmass guidance from L. Waganer.

- Minor adjustments in power requirements based on latest spreadsheet analysis FIRE_010727.xls, which is for the 10T, 2.14m machine.

- Correction to costs for DCCB system for PF plasma initiation. Although actual voltage and current requirements are still not known, prior estimate was erroneously set to equal ITER Fast Discharge Unit cost, should have been ITER Switching Network Unit cost, which is considerably less since it does not have to absorb the full coil energy.

Assumed requirements along with the updated cost are listed in the following tables.

### OVERALL POWER REQUIREMENTS

| EXPERIMENTAL POWER |  |
| --- | --- |
| Peak Active Power (MW) | 745 |
| Peak Reactive Power (MVAR) | 1091 |
| Peak Apparent Power (MVA) | 1182 |
| Peak Pulse Energy (GJ) | 14 |
| Overall Pulse Duration (second) | 55 |
| Pulse Repetition Period (minute) | 120 |
| AUXILIARY POWER |  |
| Maximum Apparent Power (MVA) | 60 |
| Maximum Emergency Power (MVA) | 3.25 |

#### CURRENT  AND VOLTATE REQURIEMENTS

|  | TF | CS1 | CS2 | CS3 | PF1 | PF2 | PF3 | PF4 | CC | FECC |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| # Systems | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 8 |
| Imax (kA) | 446 | 35 | 50 | 25 | 50 | 50 | 6 | 2 | 75 | ? |
| ¦V¦max (I>0) (kV) | 1.1 | 3.0 | 1.0 | 1.0 | 1.0 | 1.0 | 3.0 | 4.1 | 0.05 | ? |
| Imin (kA) |  | -50 |  |  |  |  | -50 | -50 |  | ? |
| ¦V¦max (I<0) (kV) |  | 3.0 |  |  |  |  | 3.0 | 4.1 |  | ? |
| Vdccb (repetitive for initiation) (kV) |  | ? | ? | ? | ? | ? | ? | ? |  |  |
| Vdccb (non-repetitive for protection) (kV) |  |  |  |  |  |  |  |  |  |  |

##### POWER SUPPLY RATINGS

|  | TF | CS1 | CS2 | CS3 | PF1 | PF2 | PF3 | PF4 | CC | FECC |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 2-Quadrant PS Req’t (MVA) | 468 |  | 50.6 | 25.3 | 50.6 | 50.6 | 18.2 | 8.1 | 7.5 | 10 |
| 4-Quadrant PS Req’t (MVA) |  | 152 |  |  |  |  | 152 | 203 |  |  |
| ∑TF (2Q) | 468 |  |  |  |  |  |  |  |  |  |
| ∑PF (2Q) | 221 |  |  |  |  |  |  |  |  |  |
| ∑PF (4Q) | 506 |  |  |  |  |  |  |  |  |  |

##### COSTS IN $2002

| CATEGORY | FIRE Rating (MVA) | FIRE Scaling ($K02 /MVA) | Fire Cost (M$02) | TR | TW | SR | SW | CR | CW | Cont % | C$ |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Utility Grid Interface | 600 | 5.6 | 3.3 | 1 | 2 | 8 | 1 | 1 | 2 | 12 | 0.4 |
| Substation | 600 | 18.2 | 10.9 | 1 | 2 | 8 | 1 | 1 | 2 | 12 | 1.3 |
| Energy Storage System | 0 |  | 0.0 | 2 | 2 | 8 | 1 | 4 | 2 | 20 | 0.0 |
| Reactive Power Compensation | 300 | 35.1 | 10.5 | 2 | 2 | 8 | 1 | 4 | 2 | 20 | 2.1 |
| ∑AC Distribution | 1579 | 3.6 | 5.7 | 1 | 2 | 8 | 1 | 1 | 2 | 12 | 0.7 |
| AC/DC Converters | 1204 |  |  |  |  |  |  |  |  |  |  |
| Auxiliary Heating | 75 |  |  |  |  |  |  |  |  |  |  |
| Reactive Compensation | 300 |  |  |  |  |  |  |  |  |  |  |
| TF AC/DC Converters | 468 | 59.7 | 27.9 | 4 | 2 | 8 | 1 | 4 | 2 | 24 | 6.7 |
| TF Fast Discharge Units | 0 |  | 0.0 |  |  |  |  |  |  |  |  |
| ∑PF AC/DC Converters | 727 |  |  |  |  |  |  |  |  |  |  |
| - 4Q AC/DC Converter | 506 | 67.4 | 34.1 | 4 | 2 | 8 | 1 | 4 | 2 | 24 | 8.2 |
| - 2Q AC/DC Converter | 221 | 59.7 | 13.2 | 4 | 2 | 8 | 1 | 4 | 2 | 24 | 3.2 |
| PF Switching Networks |  |  |  |  |  |  |  |  |  |  |  |
| -Fast Discharge Circuits |  |  | 0.0 |  |  |  |  |  |  |  |  |
| -Switching Network Units | 1350 | 2.1 | 2.8 | 6 | 2 | 8 | 1 | 6 | 2 | 32 | 0.9 |
| Fast Plasma Position Control PS | 8 | 175.6 | 1.3 | 6 | 2 | 4 | 1 | 6 | 2 | 28 | 0.4 |
| Field Error Correction PS | 1 | 100.0 | 0.1 | 2 | 2 | 4 | 1 | 6 | 2 | 20 | 0.0 |
| Instrumentation |  | n.a. | 3.5 | 6 | 2 | 8 | 1 | 4 | 2 | 28 | 1.0 |
| DC Components & Dummy Loads |  | n.a. | 22.0 | 4 | 2 | 4 | 1 | 4 | 2 | 20 | 4.4 |
| Exp Power System Engineering | 8m*6yr |  | 11.5 | 4 | 2 | 8 | 1 | 4 | 2 | 24 | 2.8 |
| TOTAL EXP PWR SYS |  |  | 146.9 |  |  |  |  |  |  | 22 | 32.0 |
| Auxiliary Power System | 60 | 120.8 | 7.2 |  |  |  |  |  |  |  |  |
| Aux Power System Engineering | 4m*6y |  | 5.8 |  |  |  |  |  |  |  |  |
| TOTAL AUX POWER SYSTEM |  |  | 13.0 | 1 | 2 | 8 | 1 | 4 | 2 | 18 | 2.3 |
| GRAND TOTAL |  |  | 159.9 |  |  |  |  |  |  |  | 34.3 |