## NSTX Loop Resistances.xls
TF cable resistances
Length 1000mcm cables per leg | Parallels | Resistance/ ft at 25°C | Length of 750 mcm Cables per leg SDS to waterfall | Length of 750 mcm Cables PSS to SDS per leg & PSS to PSS | Resistance/ ft at 25°C | Parallels in each of four paths | Resistance from Waterfall to Hot Cell both legs | Resistance from SDS to Waterfall both legs per parallel ckt of 4 | Resistance from PSS to SDS both legs per parallel ckt of 4 (included PSS to PSS) | Total Loop Resistance of Cabling at 25°C | Voltage Drop at 73.3kA
225 | 6 | 1.11e-05 | 110 | 506.7571 | 1.48e-05 | 6 | 0.0008325 | 0.00054267 | 0.0025 | 0.0015932 | 116.7791
Note: Loop resistance is computed by dividing the resistance of PSS to waterfall area by 4 and then adding the resistance from
waterfall to Hot çell
OH cable resistances
Length 1000 mcm cables per leg | Parallels | Resistance/ ft at 25°C | Length of 750 mcm Cables per leg SDS to waterfall | Length of 750 mcm Cables PSS to SDS per leg & PSS to PSS | Resistance/ ft at 25°C | Parallels in each of four paths | Resistance from Waterfall to Hot Cell both legs | Resistance from SDS to Waterfall both legs per series/parallel ckt of 4 | Resistance from PSS to SDS both legs per series/parallel ckt of 4 (included PSS to PSS) | Total Loop Resistance of Cabling at 25°C | Voltage Drop at 24kA
225 | 1 | 1.11e-05 | 110 | 506.7571 | 1.48e-05 | 6 | 0.004995 | 0.00054267 | 0.0025 | 0.0080377 | 192.904
Note: Loop resistance is computed by multiplying the resistance of PSS to waterfall area by 2 and then adding the resistance from
waterfall to Hot çell