5X-980112-CLN-01

TO: DISTRIBUTION

FROM: C NEUMEYER
SUBJECT:  PEER REVIEW ON NSTX TEST CELL & PLATFORM GROUNDING

A successful peer review covering the NSTX Test Cell and Platform Grounding scheme was held on 12 January.

Attendees were as follows:

R Borusovic

G Labik

B Mc Cormack

M Ono

S Ramakrishnan

M Viola

Four chits were generated as follows:

| Chit | Dispostion | Action |
| --- | --- | --- |
| 1) The (existing) west ground bus bar gets its ground from the east wall. Do not connect floor bar to the west wall. | Disagree; disconnect existing east to west jumper and connect west wall bus to the floor bar. | WBS 5 (S Ramakrishnan) to include in Installation Procedure for Grounding. |
| 2) Provide 18" x 18" x 1/2" copper plate at the center. | Agree; this is required to accept the various connections to the central "single point ground" | WBS 5 (S Ramakrishnan) to include in drawings and Installation Procedure for Grounding. |
| 3) Check/map the resistance of the various platform elements prior to grounding. | Agree; need to perform dielectric test on beam to beam and beam to column gaps prior to jumpering, as well as column to facility ground (through floor concrete). | WBS 5 (S Ramakrishnan) to include in Installation Procedure for Grounding. |
| 4) Provide diagnostics/instrument ground bus on east wall, connected directly to central grounding plate. | Agree; will eliminate concern about noise due to potentials from power currents returning through the east-west floor bar. | WBS 5 (S Ramakrishnan) to include in drawings and Installation Procedure for Grounding. |

It is noted here that, following the meeting, an inspection of the NSTX Test Cell revealed that the existing ground bus bars on the walls are 1/4" x 2". This is less than the 4" width discussed for the floor bars at the review. However, the 2" width is adequate. As indicated in the table below, the resultant 0.5 sq in cross section will not overheat under the worst case fault conditions (faults driven by the FCPC power supplies). Still, the 4" width shall be maintained for the floor bus to minimize the impedance.

|  | Cable | Bar | Bar |  |
| --- | --- | --- | --- | --- |
| Cond resistivity @ 20C | 1.73E-06 | 1.73E-06 | 1.73E-06 | Ω-cm |
| Cond res temp coeff | 0.00393 | 0.00393 | 0.00393 | 1/degC |
| Cond heat capacity | 0.386 | 0.386 | 0.386 | J/gm-degC |
| Cond density | 8.89 | 8.89 | 8.89 | gm/cc |
| Ambient Temperature | 30.0 | 30.0 | 30.0 | deg C |
| Max Current | 120000.0 | 120000.0 | 120000.0 | amp |
| Min ESW | 0.080 | 0.080 | 0.080 | sec |
| Max ∫i^2dt | 1.15E+09 | 1.15E+09 | 1.15E+09 | A^2-s |
| CSA | 500.0 |  |  | MCM |
|  | 0.4 | 1.0 | 0.5 | sq in |
|  | 2.5335 | 6.4516 | 3.2258 | sq cm |
| # Conductors | 1 | 1 | 1 |  |
| Total CSA | 2.5335 | 6.4516 | 3.2258 | sq cm |
| Allowable Tmax | 200.0 | 200.0 | 200.0 | degC |
| Res per inch @ Tmax | 2.96E-06 | 1.16E-06 | 2.32E-06 | Ω |
| Thermal Capacitance per inch | 22.1 | 56.2 | 28.1 | Joule/degC-in |
| Adiabatic Temp rise per pulse | 154.3 | 23.8 | 95.2 | deg C |

Presentation materials and chit forms are attached.

R Borusovic*

G Labik*

B Mc Cormack*

M Ono*

E Perry*

S Ramakrishnan*

M Viola*

NSTX File

* = w/o attachments