National Spherical Tokamak Experiment

NSTX

SYSTEM REQUIREMENTS DOCUMENT

Auxiliary Systems

NSTX-SRD-3X-021

Revision 0

July 12, 1996

________________________________

Robert Parsells

WBS 3 Manager

________________________________

Charles Neumeyer

NSTX Project Engineering Manager

________________________________

Masa Ono

NSTX Project Manager

| Revision | Date | TRB | Description of Change |
| --- | --- | --- | --- |

| 0 | 7/12/96 |  | Initial Release |
| --- | --- | --- | --- |

WBS 3.0 - Auxiliary Systems Requirements	3

WBS 3.1 - Vacuum Pumping System (VPS)	4

3.1.1 Functions	4

3.1.2 Configuration Requirements & Essential Features	4

3.1.3 Performance & Operational Requirements	5

3.1.3.1 Baseline Operation	5

3.1.3.2 Upgrades	5

WBS 3.2 - Gas Delivery System (GDS)	6

3.2.1 Functions	6

3.2.3 Configuration Requirements & Essential Features	6

3.2.3 Performance & Operational Requirements	6

3.2.3.1 Baseline Operation	6

3.2.3.2 Upgrades	6

WBS 3.3 - Glow Discharge System (GDS)	7

3.3.1 Functions	7

3.3.2 Configuration Requirements & Essential Features	7

3.3.3 Performance & Operational Requirements	7

WBS 3.4 - Cooling Water System (CWS)	8

3.4.1 Functions	8

3.4.2 Configuration Requirements & Essential Features	8

3.4.3 Performance & Operational Requirements	8

3.4.3.1 Baseline Operation	8

3.4.3.3 Upgrades	9

WBS 3.5 - Bakeout System	10

3.5.1 Functions	10

3.5.2 Configuration Requirements & Essential Features	10

3.5.3 Performance & Operational Requirements	10

WBS 3.0 - Auxiliary Systems Requirements

The auxiliary systems consist of the vacuum pumping system (WBS 3.1), the gas delivery system (WBS 3.2), the glow discharge system (WBS 3.3), the coolant system (WBS 3.4),  and the bakeout heating system (WBS 3.5). The requirements for each of the four wbs systems are given in the following sections.

WBS 3.1 - Vacuum Pumping System (VPS)

3.1.1 Functions

a.	The NSTX vacuum system establishes and maintains, the vacuum environment within the NSTX vacuum vessel.  It consists of a pumping system, associated piping and valves capable of achieving high vacuum, various pressure sensing elements and transducers, and an analytical system capable of discriminating gas species.

b.	The NSTX vacuum system shall perform the following functions:

•	Roughdown of the NSTX device from atmosphere to base pressure.

•	Provide a high vacuum environment compatible with the NSTX experimental program.

•	Remove plasma exhausts and restore base pressure between pulses.

•	Minimize and maintain impurity levels as required.

•	Provide analytical capability for monitoring and control of machine vacuum condition.

•	Provide pumping and control of pressure for Glow Discharge/Pulse Discharge Cleaning modes (GDC/PDC).

•	Be compatible with, and provide pumping for vacuum vessel bakeout.

•	Provide appropriate safety interlocks for personnel and equipment safety.

3.1.2 Configuration Requirements & Essential Features

a.	The vacuum pumping system shall consist of a pair of water-cooled turbo molecular (momentum transfer) pumps and at least one positive displacement mechanical pump.

b.	The mechanical pumps shall be capable of evacuating the NSTX vacuum vessel from atmosphere to 1 x 10-3 Torr [R1], and are capable of backing the turbomolecular pumps when base pressure is achieved.

c.	The Turbomolecular pumps shall be capable of achieving a base pressure of 1x10-9 Torr [R2], and evacuating spent plasma gasses between pulses.

d.	Turbomolecular pumps, as well as the RGA and vacuum vessel pressure gauges shall be located on, or close to the vacuum vessel to maximize conductance.

e.	Pressure gauges capable of monitoring pressure from atmosphere to high vacuum shall be located on the vacuum vessel or appropriate appendages.

f.	Redundant Residual Gas Analyzers (RGA) [R4] capable of discriminating gas species shall be employed. Capability for monitoring and remote control of machine vacuum and vacuum system components from the control room shall be provided.

g.	Service ports, strategically located on the vacuum system and the vacuum vessel, shall be provided to facilitate maintenance and leak checking.

3.1.3 Performance & Operational Requirements

3.1.3.1 Baseline Operation

a.	The roughing pump(s) shall be capable of evacuating the vacuum vessel from atmosphere to 1x10-3 Torr in less than 3 hours [R1].

b.	The vacuum system shall be capable of achieving a base pressure of 1x10-9 Torr or lower [R2].

c.	The system shall be capable of evacuating plasma gas loads and establishing base pressure between machine pulses (5 minutes) [R3].

d.	The  high vacuum pressure sensing element shall be capable of providing real time feedback to the gas injection system.

e.	The RGA system is able to scan and provide resolution of 1x10-11 Torr partial pressure for masses 1 to 60.

f.	Individual vacuum system components have a leak rate no greater than 1x10-9 sccs air equivalent as measure by a Helium Mass Spectrometer Leak Detector (HMSLD).  The total aggregate leak rate for the NSTX Vacuum vessel/vacuum system shall not exceed 1x10-6 sccs air equivalent.

g.	The vacuum system shall be capable of maintaining a pressure of 1x10-4 Torr during GDC.

3.1.3.2 Upgrades

a.	Provisions for additional pumping capacity for neutral beam enclosures shall be considered in the baseline design [R5].

b.	Provision for expansion of the vacuum system for long pulse operation shall be considered into the baseline design [R5].

WBS 3.2 - Gas Delivery System (GDS)

3.2.1 Functions

a.	The Gas Delivery System (GDS) shall provide the following functions:

•	Provide gas for plasma fueling.

•	Provide gas for GDC.

•	Provide instrumentation and control for gas injection

•	Provide capability to select gas to be injected.

3.2.3 Configuration Requirements & Essential Features

a.	The following features shall be incorporated into the GDS design:

•	A gas bottle bank with manifolding to allow user selection of three different gasses.

•	Three gas injection points on the vacuum vessel.

•	Injection valves with less than 10 millisecond response time allowing feedback for real time control.

•	Minimization or elimination of explosive mixtures in the system piping and hardware.

•	Remote operation and calibration of system.

3.2.3 Performance & Operational Requirements

3.2.3.1 Baseline Operation

a.	The vacuum pumping system shall be capable of providing a flow rate of at least 50 Torr-liters/sec [R6].

b.	The throughput leakage shall be less than 1 x 10-9 sccs air equivalent.

3.2.3.2 Upgrades

a.	Provisions for long pulse operations shall be considered in the baseline design [R5].

b.	Provisions for Neutral Beam gas injection requirements shall be considered in the baseline design [R5].

WBS 3.3 - Glow Discharge System (GDS)

3.3.1 Functions

The Glow Discharge Cleaning System (GDC) establishes and controls the GDC process in NSTX. GDC  is a mode of vacuum conditioning in which vacuum vessel internal surfaces are “scrubbed” clean by the bombardment of ions formed during the glow process. The GDC system is highly integrated with the VPS and GDS.

3.3.2 Configuration Requirements & Essential Features

a.	The following features shall be incorporated into the GDC design:

•	An in-vessel probe which acts as the anode.

•	Power supply for the anode probe.

•	Instrumentation and control for operation.

•	The GDS shall be remotely configurable and operable.

•	The GDS shall be capable of operating with helium and helium/oxygen mixtures.

•	The GDS system shall be capable of steady state operation.

3.3.3 Performance & Operational Requirements

The GDC operating parameters are shown in Table GDS- 3.3.3-1

Table GDS-3.3.3-1: GDC Operating Parameters

| Parameter | Value | Units | Reference |
| --- | --- | --- | --- |

| Voltage | 400 | volts | [R8] |
| --- | --- | --- | --- |

| Current | 20 | amperes | [R8] |
| --- | --- | --- | --- |

| Throughput | 44 | Torr-l/s | [R7] |
| --- | --- | --- | --- |

WBS 3.4 - Cooling Water System (CWS)

3.4.1 Functions

a. The cooling water system shall provide active cooling and over-heating protection for the coil systems, the power supply systems, the component cooling system, and the heating systems that support NSTX.

b. Specific functions include:

• Provide chilled, de ionized water for heat removal in the TF, OH and PF coils.

• Provide chilled, de ionized water for the RF sources, in vessel components, power supplies, bus bar systems, and various diagnostics.

• Provide Flow switches to prevent damage due to loss of flow.

• Accommodate, as practical, future requirements on the system to support Neutral Beam operations.

c. The C-site MG system incorporates its own cooling water system, and is therefore does not require a water supply from WBS 3.4

3.4.2 Configuration Requirements & Essential Features

a.	The cooling water system shall utilize existing equipment located in the C-Site basement [R12]. The cooling water pumps, heat exchanger and tank shall not infringe on the space in the NSTX test cell.

b.	One high pressure booster pump is required for the OH cooling water supply.

c.	Sufficient instrumentation or the capability to add instrumentation shall be provided to troubleshoot individual coil flow paths [R13].

d.	The dew point in the test cell shall be monitored to prevent condensation.

e.	The conductivity of the de ionized water shall be measured to verify it is within acceptable limits.

f.	All materials in the cooling water system shall be selected for operation in de ionized water.

g.	A flow switch shall be provided for each coil flow path [R13].

h.	A local processor shall receive flow switch inputs and provide data to the central I&C, indicating the status of each individual flow switch.

i.	Valves and Pumps shall be controlled locally and from the C-site MG area.

3.4.3 Performance & Operational Requirements

3.4.3.1 Baseline Operation

a.	For coils where the exit cooling water temperature may exceed 100°C the water pressure shall be maintained at the pressure required to prevent boiling.

b.	The system shall provide cooling water to the TF, PF and OH coils as specified in Table CWS-3.4.3.1-1.

Table CWS-3.4.3.1-1: NSTX Coil Cooling Water Requirements [R15,R16]

| SYSTEM | TOTAL FLOW (GPM) | INLET PRESSURE (psig) | OUTLET PRESSURE (psig) | HEAT LOAD (MJ/pulse) (Note 1) | HEAT LOAD (kW Avg.) (Note 2) |
| --- | --- | --- | --- | --- | --- |

| OH I Coils | 3 | 450 | 50 | inc'l below | inc'l below |
| --- | --- | --- | --- | --- | --- |

| OH II and PF Coils | 50 | 110 | 0 | 56.9 | 159.1 |
| --- | --- | --- | --- | --- | --- |

| TF Coils | 233 | 55 | 50 | 45.3 | 151.1 |
| --- | --- | --- | --- | --- | --- |

| Total | 286 |  |  | 103 | 310 |
| --- | --- | --- | --- | --- | --- |

Note 1: Assumes all PF/OH coils at max. current rating, inductive pulse

Note 2: Assumes all PF coils at max. current rating, rated duty cycle, non-inductive pulse

c.	The cooling water inlet temperature shall be less than 20°C but greater than 14°C so as not to drop below the dew point in the test cell.

d.	The resistivity of the water must be maintained at greater than 1 mega ohms cm.

e.	Cooling water to the power systems shall be provided as specified in Table CWS-3.2.3.1-2.

Table 3.4.3.2 Power Supply Cooling Water Requirements [R14]

| Power Supply | Units | FLOW (GPM) | Pressure Drop (psig) | Heat Load (kW during pulse) | Heat Load (avg. kW) |
| --- | --- | --- | --- | --- | --- |

| Transrex 24 kA Rectifier | 2 | 64 | 100 | 203 | 3.4 |
| --- | --- | --- | --- | --- | --- |

| Robicon 5 kA Rectifiers | 4 | 3 | 100 | 30 | 0.5 |
| --- | --- | --- | --- | --- | --- |

| Robicon 10 kA Rectifiers | 1 | 3 | 100 | 60 | 1 |
| --- | --- | --- | --- | --- | --- |

| Robicon 20 kA Rectifiers | 1 | 3 | 100 | 120 | 2 |
| --- | --- | --- | --- | --- | --- |

| DC Bus Bars | 1 | 9 | 35 | 128 | 30 |
| --- | --- | --- | --- | --- | --- |

| Totals |  | 155 |  | 835 | 41.7 |
| --- | --- | --- | --- | --- | --- |

3.4.3.3 Upgrades

Per section 2.1.3 of the GRD, upgrades for the water system need not be considered.  There is however a large surplus capacity in the existing water system capable of providing approximately 4800 GPM at 110 psig.

WBS 3.5 - Bakeout System

3.5.1 Functions

a.	The assembled vessel shall have a heating system with in situ bakeout for the vessel and for the tiles. During this procedure, the gases absorbed and diffused within the vessel material are released and subsequently removed from the vessel by the Torus Vacuum Pumping System.

b.	A vacuum vessel heating/cooling system shall provide for heating the vessel during the bakeout mode of operation, and cooling the vessel during long pulse operation. The port covers shall be maintained to an even temperature distribution during bakeout.

3.5.2 Configuration Requirements & Essential Features

a.	Flexible insulating blankets with electric strip heaters shall be mounted on the vacuum vessel exterior to provide a means to heat and thermally insulate the vessel.

b.	Water cooling panels shall be mounted on the vacuum vessel exterior to provide a means to cool the vessel during bakeout.

c.	Thermocouples shall be attached to the vacuum vessel walls to provide a means to control the heating system.

d.	The bake out heating system shall insulate personnel from heated surfaces.

e.	The physical interface for the bakeout heating system is the torus interface valve.

3.5.3 Performance & Operational Requirements

3.5.3.1 Baseline Operation

a.	Insulating blankets and bake out heaters shall bring the vacuum vessel to the required 150 C [R9] bakeout temperature within 48 hrs [R11].

b.	Heaters, inserted through torus interface valves, shall bring carbon tiles to the specified bake out temperature of 350 C [R10] within 48 hrs [R11].

c.	Water cooling panels shall maintain the vacuum vessel at the specified bake out temperature of 150 C [R9] during bakeout and long pulse operation.

d.	The bake out system shall be capable of holding bake out temperature for up to TBD hours minimum at an average frequency of TBD times per year.

3.5.3.2 Upgrades

a.	Long pulse operation will require active cooling of the vacuum vessel by the bake out system.

| R | Description | Value | Units | Reference |
| --- | --- | --- | --- | --- |

| 1 | Vacuum and Wall conditioning | n/a | n/a | GRD: 2.3.1.c |
| --- | --- | --- | --- | --- |

| 2 | Vacuum and Wall conditioning | n/a | n/a | GRD: 2.3.1.a |
| --- | --- | --- | --- | --- |

| 3 | Vacuum and Wall conditioning | n/a | n/a | GRD: 2.3.1.d |
| --- | --- | --- | --- | --- |

| 4 | Vacuum Pumping System (VPS) | n/a | n/a | GRD: 1.4.1.b |
| --- | --- | --- | --- | --- |

| 5 | Design Basis and Upgrades | n/a | n/a | GRD: 1.1.2.b |
| --- | --- | --- | --- | --- |

| 6 | Fueling | n/a | n/a | GRD: 2.4.1.a |
| --- | --- | --- | --- | --- |

| 7 | Vacuum and Wall conditioning | n/a | n/a | GRD: 2.3.3.a |
| --- | --- | --- | --- | --- |

| 8 | Vacuum and Wall conditioning | n/a | n/a | PRD: 1.9.3 |
| --- | --- | --- | --- | --- |

| 9 | VV surfaces bakeout | 150 | oC | GRD: 2.3.2.b |
| --- | --- | --- | --- | --- |

| 10 | PFC surfaces bakeout | 350 | oC | GRD: 2.3.2.a PRD: 1.9.2 |
| --- | --- | --- | --- | --- |

| 11 | Bakeout heating time | 48 | hrs | GRD: 2.3.2.c |
| --- | --- | --- | --- | --- |

| 12 | Existing equipment utilization | n/a | n/a | GRD: 1.4.2.a |
| --- | --- | --- | --- | --- |

| 13 | Flow switch per flow path | n/a | n/a | GRD: 1.4.2.b |
| --- | --- | --- | --- | --- |

| 14 | Power Supply Cooling Wtr Reqmts | n/a | n/a | WBS5:Table PS-3.1-2 |
| --- | --- | --- | --- | --- |

| 15 | PF Coil Cooling Water Requirements | n/a | n/a | PF Coil Spreadsheet |
| --- | --- | --- | --- | --- |

| 16 | TF Coil Cooling Water Requirements | n/a | n/a | TF Coil Spreadsheet |
| --- | --- | --- | --- | --- |

| 17 |  |  |  |  |
| --- | --- | --- | --- | --- |

| 18 |  |  |  |  |
| --- | --- | --- | --- | --- |

| 19 |  |  |  |  |
| --- | --- | --- | --- | --- |

| 20 |  |  |  |  |
| --- | --- | --- | --- | --- |

| 21 |  |  |  |  |
| --- | --- | --- | --- | --- |

| 22 |  |  |  |  |
| --- | --- | --- | --- | --- |

| 23 |  |  |  |  |
| --- | --- | --- | --- | --- |

| 24 |  |  |  |  |
| --- | --- | --- | --- | --- |

| 25 |  |  |  |  |
| --- | --- | --- | --- | --- |

| 26 |  |  |  |  |
| --- | --- | --- | --- | --- |

| 27 |  |  |  |  |
| --- | --- | --- | --- | --- |

| 28 |  |  |  |  |
| --- | --- | --- | --- | --- |

| 29 |  |  |  |  |
| --- | --- | --- | --- | --- |

| 30 |  |  |  |  |
| --- | --- | --- | --- | --- |