National Spherical Tokamak Experiment

NSTX

SYSTEM REQUIREMENTS DOCUMENT

POWER SYSTEMS

NSTX-SRD-5X-YYY

Revision 0

July 11, 1996

________________________________

Charles Neumeyer

WBS 5 Manager,

NSTX Project Engineering Manager

________________________________

Masa Ono

NSTX Project Manager

| Revision | Date | TRB | Description of Change |
| --- | --- | --- | --- |

Introduction	1

General Power System Requirements	2

1.0 Functions	2

2.0 Configuration Requirements & Essential Features	2

3.0 Performance & Operational Requirements	2

3.1 Baseline Operation	2

3.2 Upgrades	3

3.3 Pulse Repetition Period & Operating Life	4

AC Power System Requirements	5

1.0 Functions	5

1.1 Specific Functions of the Experimental AC Power System	5

1.2 Specific Functions of the Auxiliary Systems AC Power System	5

2.0 Configuration Requirements & Essential Features	6

3.0 Performance & Operational Requirements	7

3.1 Composite AC Power Load	7

3.2 Experimental Power Component of Load	8

3.3 Auxiliary Systems Component of Load	10

Toroidal Field (TF) Power Conversion Requirements	11

1.0 Functions	11

2.0 Configuration Requirements & Essential Features	11

3.0 Performance & Operational Requirements	11

3.1 Baseline Operation	11

3.1 Upgrades	13

Poloidal Field/Ohmic Heating (PF/OH) Requirements	14

1.0 Functions	14

2.0 Configuration Requirements & Essential Features	14

3.0 Performance & Operational Requirements	15

3.1 Description of PF/OH Coils	15

3.2 Baseline Operation	16

3.2.1 Plasma Equilibria Requirements	16

3.2.2 Plasma Scenario Requirements	16

3.2.3 Other Requirements	18

3.2 Upgrades	18

CHI Power Conversion System Requirements	19

1.0 Functions	19

2.0 Configuration Requirements & Essential Features	19

3.0 Performance & Operational Requirements	19

3.1 Baseline Operation	19

3.2 Upgrades	21

List of Tables

PS-3.1-1: NSTX Plasma Scenarios	2

PS-3.1-2: Inductive Pulse Duty Cycle	3

PS-3.1-3: Partial & Non-Inductive Pulse Duty Cycle	3

PS-3.1-4: Upgrade NSTX Duty Cycle	4

AC-3.1-1: Composite AC Input Power Requirements	7

AC-3.2-1: Experimental Power Loads	9

AC-3.3-1: Auxiliary Power Loads	10

TF-3.1.-1: TF Requirements	12

TF-3.1.-2 TF Ampacity Requirements	13

PF-2.0-1: Galvanically Separate PF Circuits	14

PF-3.1-1: PF/OH Coil Geometry	15

PF-3.1-2: PF Conductor Properties	15

PF-3.1-2: PF Circuit Resistances	16

PF-3.1-3: PF Mutual Inductance Matrix (mH)	16

PF-3.2-1: PF Ampacity Requirements	18

PF-3.2-2: PF Measurement and Control Accuracy Requirements	18

CHI-3.1-1 CHI Power System Requirements	20

List of FIGURES

AC-2.2.1-1: Equivalent Circuit for Utility Grid Interface	6

PF-3.2-1: OH Current Waveform	17

PF-3.2-2: OH Voltage Waveform	17

CHI-3.1-1: CHI Capacitor Discharge Current Waveform	21

APPENDIX

LIST OF REFERENCES

Introduction

This System Requirements Document (SRD) defines the requirements and design of the Power Systems (WBS 5X) of the National Spherical Tokamak Experiment (NSTX).

A general section covers information which is relevant to the entire WBS element. Individual  subelements of the WBS Sample work scope are covered in separate sections, namely:

• WBS 51 AC Power Systems

• WBS 52 Toroidal Field (TF) Power Conversion System

• WBS 53 Poloidal Field/Ohmic Heating (PF/OH) Power Conversion System

• WBS 54 Coaxial Helicity Injection (CHI) Power Conversion System

Figures and Tables are numbered in format X-Y-Z where X=section (i.e. section abbreviation, e.g. PS for Power System), Y=paragraph number, and Z= sequence number within that paragraph.

References to the requirements identified herein are cited in the body of the document using serial numbers preceded by an "R" and are listed in the Appendix.

WBS 5X -  General Power System Requirements

1.0 Functions

The Power Systems WBS element is required to supply and deliver all electrical power to equipment associated with the NSTX.

2.0 Configuration Requirements & Essential Features

a. The NSTX machine shall be installed at the PPPL C-site C-1 area (formerly occupied by the Princeton Large Torus (PLT)) [R1]. The C-site power supply resources shall be utilized to the maximum extent for NSTX operation [R2].

b. Transfer switches shall be provided to allow the shared usage of power supplies which serve both NSTX and PBX-M [R2].

c. Controls and interlocks shall be designed to accommodate shared usage between NSTX and PBX-M [R2].

3.0 Performance & Operational Requirements

a. The baseline design of NSTX shall not preclude the possibility of the upgrades, and shall facilitate the upgrades whenever possible and cost effective. However, for the Power Systems, none of the upgrade features are required to be incorporated in the baseline design of NSTX [R3].

b. The anticipated upgrades include the following [R3]:

• CHI current sustainment power supply

• addition of neutral beam injection (NBI)

• long pulse operation (with center stack replacement)

3.1 Baseline Operation

Baseline:

a. Baseline NSTX operation involves five basic scenarios, as listed in Table PS-3.1-1. [R4]:

Table PS-3.1-1: NSTX Plasma Scenarios

| SCENARIO | START-UP | SUSTAINMENT | CONFIGURATION |
| --- | --- | --- | --- |

| I | OH | OH | ND, DN |
| --- | --- | --- | --- |

| II | OH (Half-Swing) | HHFW | ND, DN |
| --- | --- | --- | --- |

| III | CHI |  | SN |
| --- | --- | --- | --- |

|  |  | OH, HHFW | ND, DN, SN |
| --- | --- | --- | --- |

| IV | OH (Half-Swing) |  | ND, DN, SN |
| --- | --- | --- | --- |

|  |  | CHI, HHFW | SN |
| --- | --- | --- | --- |

| V | CHI | CHI, HHFW | SN |
| --- | --- | --- | --- |

b. Start Up refers to the initiation and drive of plasma current up to flat top. Sustainment refers to the drive of plasma current during flat top. Configuration refers to the plasma shape, either Natural Divertor (ND) (a.k.a. limiter), Double Null (DN) divertor, or Single Null (SN) divertor.

c. Scenario I is fully inductive (initiates and drives plasma current via inductive means only) and requires a full swing of the OH current from maximum positive to maximum negative value. Scenarios II, III,  and IV are partially inductive (initiate and/or drive plasma current via inductive means). Scenario V is non-inductive (requires no inductive plasma initiation or current drive).

d. As indicated in Table PS-3.1-1, for any scenario one or more sustainment current drive techniques may be used, and one or more configurations may be employed. However, the OH and CHI operations are mutually exclusive, and the CHI operation requires a SN plasma configuration.

e. The basic duty cycle of the inductive scenario (Scenario I) is defined in Table PS-3.1-2:

Table PS-3.1-2: Inductive Pulse Duty Cycle

| Parameter | Value | Units | Ref |
| --- | --- | --- | --- |

| Inductive Maximum Pulse Length | 0.5 | sec | 19 |
| --- | --- | --- | --- |

| Inductive Minimum Repetition Period | 600.0 | sec | 20 |
| --- | --- | --- | --- |

f. The basic duty cycle of the partial and non-inductive scenarios (Scenario II, III, IV, and V) is defined in Table PS-3.1-3:

Table PS-3.1-3: Partial and Non-Inductive Pulse Duty Cycle

| Parameter | Value | Units | Ref |
| --- | --- | --- | --- |

| Non-Inductive Maximum Pulse Length | 5.0 | sec | 21 |
| --- | --- | --- | --- |

| Non-Inductive Minimum Repetition Period | 300.0 | sec | 22 |
| --- | --- | --- | --- |

g. Baseline Heating and Current Drive (H&CD) mix is as follows:

- High Harmonic Fast Wave Current Drive (HHFW)

- Coaxial Helicity Injection (CHI)

- Electron Cyclotron Heating (ECH)

h. In the baseline configuration the CHI shall provide current drive during the start up phase only, and shall be accomplished via a capacitor bank discharge.

3.2 Upgrades

3.2.1 CHI Current Sustainment Power Supply [R5]

a. The Power Systems design shall consider an upgrade which would provide a power supply to provide CHI current drive sustainment for the full plasma flat top duration.

b. The baseline design for the Power Systems shall identify an upgrade path for the CHI current sustainment mode.

3.2.2 Neutral Beam Injection (NBI) Upgrade [R5]

a. The Power Systems design shall consider an upgrade which would place the four existing PBX-M sources on NSTX.

b. The baseline design for the Power Systems shall identify an upgrade path for the neutral beam upgrade.

3.2.3 Long Pulse Upgrade [R5]

a. The Power Systems design shall consider an upgrade which would remove the baseline TF and OH magnets, and place a new TF magnet in the center stack. The NSTX plasma pulse length shall be assumed to be 60 seconds for this upgrade.

b. The baseline design for the Power Systems shall identify an upgrade path for the long pulse operation. The assumed repetition period shall be as indicated in Table PS-3.2-1, which would (at the same pulse current magnitude as the baseline) result in the same rms current as the baseline.

Table PS-3.2-1: Upgrade NSTX Duty Cycle

| Parameter | Value | Units | Ref |
| --- | --- | --- | --- |

| Upgrade Maximum Pulse Length | 60.0 | sec | 23 |
| --- | --- | --- | --- |

| Upgrade Minimum Repetition Period | 3600.0 | sec | 24 |
| --- | --- | --- | --- |

3.3 Pulse Repetition Period & Operating Life

a. The baseline Power Systems shall be designed to produce a maximum of 100 pulses per 24 hour period [R6]

b. The Power Systems shall be designed to operate for a period of 10 years [R6].

c. NSTX operation shall be assumed to consist of 100 pulses per day, 5 days per week, 3 weeks per month, 9 months per year, for 10 years (total of 135,000 pulses). Non-operating times are available for maintenance [R6].

WBS 51 -  AC Power System Requirements

The AC Power System WBS Element (WBS 51) is divided into two major subelements, namely the Experimental AC Power System (WBS 511, which includes all loads due to TF, PF,  and H&CD systems) and the Auxiliary Systems AC Power System (WBS 512, which includes all NSTX auxiliary or "house" power demands).

1.0 Functions

a. The function of the AC Power System is to provide the source of all electric power required for the NSTX facility.  The AC Power System must establish the connection between the PPPL facility and the local utility network in a fashion which permits the pulsed loading required by the NSTX experiment while maintaining a power source of suitable quality for existing house loads.

b. Experimental operation of the NSTX facility shall not be coincident with the operation of other major machines at PPPL (TFTR, PBX-M). Provision shall be included to prevent simultaneous operation to the extent that limits on power delivery to PPPL could be exceeded [R7].

1.1 Specific Functions of the Experimental AC Power System

The specific functions of the Experimental AC Power System include:

a. Delivery of power to C-Site 4.16kV Q1, Q2, Q3, Q4 and Q6 bus, from 	secondary AC terminals of XQT-1 and XQT-2 to Q buses.

b. Delivery of power to C-Site 13.8kV S4 bus (new) from secondary terminals of

XST-2 to S4 bus.

c. AC distribution from Q1 and Q2 bus to the C-site MG equipment

d. AC distribution from Q1 bus to ESAT building rectifier equipment via

Q1-B5 feeder.

e. AC distribution from Q6 bus to H&CD converter transformer primary AC input 	terminals.

f. AC distribution from S4 bus to OH converter transformer primary terminals

1.2 Specific Functions of the Auxiliary Systems AC Power System

The specific functions of the Auxiliary Systems AC Power System include:

a.  All auxiliary system AC distribution at C-Site pertaining to the NSTX operations, from Q3 and Q4  bus to points of utilization at 4.16kV, 480V, 208V, and 120VAC levels.

c. Standby power diesel generator and all associated equipment.

d. UPS systems and all associated equipment.

2.0 Configuration Requirements & Essential Features

a. All input power shall be derived from the 138kV service incoming to the laboratory.

b. The electrical utility service to the Princeton Plasma Physics Laboratory (PPPL) site is a 138 kV transmission line thermally rated at 600 Amp steady state (equivalent to roughly 140 MVA). Present agreements with the local utility, Public Service Electric and Gas (PSE&G) permit PPPL to take a 120 MVA dynamic load without phase correction.

c. The limitation on pulsed loading of the utility service is determined by the regulatory requirements regarding the voltage variation experienced by other customers as a result of the pulsed load. The utility considers a +/-1% variation at the nearest point of connection to other customers to be acceptable.

d. PPPL's pulsing affects other PPPL's loads which derive power from the 138kV system as well, some of which (such as computer systems) are voltage sensitive. For that reason the dynamic voltage variation at PPPL's 138 kV bus (on pulsing) shall be held to +/-3% or better. The composite loads imposed by NSTX and the remainder of PPPL need to be accommodated, as well as fault transients due to short circuits, load sheds etc.

e. The equivalent circuit given in Figure AC-1-1 shall be utilized for voltage drop and short circuit calculations [R8].

Figure AC-2.2.1-1: Equivalent Circuit for Utility Grid Interface

g. All Auxiliary Power Systems loads shall nominally be powered from the utility power source via XQT-1 and distributed via buses Q3 and Q4.

h. Standard Auxiliary Power Systems services shall be as follows:

• Service voltages (3-phase)		13.8kV, 4.16kV, 480V, 208V

• Service voltages (single phase) 	120V

i. A subset of the Auxiliary Power Systems loads require automatic transfer to the standby (diesel generator) power source in the event of a loss of site power from the 138kV service.

j. A subset of the Auxiliary Power Systems loads require uninterruptable power supplies (UPS).

3.0 Performance & Operational Requirements

3.1 Composite AC Power Load

Table AC-3.1-1 describes the requirements for total (composite) input power, as measured at the 138kV utility interface with PPPL.

Table AC-3.1-1: Composite AC Input Power Requirements

| Load | MVA | p.f | MW | MVAR | Ref |
| --- | --- | --- | --- | --- | --- |

| Baseline |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |

| NSTX Exp AC Power (between pulses) | 1.18 | 0.80 | 0.95 | 0.70 | AC-3.2-1 |
| --- | --- | --- | --- | --- | --- |

| NSTX Exp AC Power (during pulses) | 121.90 | 0.84 | 102.00 | 66.75 | AC-3.2-1 |
| --- | --- | --- | --- | --- | --- |

| NSTX Aux Sys AC Power | 3.50 | 0.80 | 2.80 | 2.10 | AC-3.3-1 |
| --- | --- | --- | --- | --- | --- |

| PPPL House Power (A,B,C,D-sites) | 8.75 | 0.80 | 7.00 | 5.25 | 27 |
| --- | --- | --- | --- | --- | --- |

| Base load between pulses | 13.43 | 0.80 | 10.75 | 8.05 |  |
| --- | --- | --- | --- | --- | --- |

| Pulsed load | 121.90 | 0.84 | 102.00 | 66.75 |  |
| --- | --- | --- | --- | --- | --- |

| Peak load during pulses | 134.13 | 0.83 | 111.80 | 74.10 |  |
| --- | --- | --- | --- | --- | --- |

| NBI Upgrade |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |

| NSTX Exp AC Power (between pulses) | 1.18 | 0.80 | 0.95 | 0.70 | AC-3.2-1 |
| --- | --- | --- | --- | --- | --- |

| NSTX Exp AC Power (during pulses) | 143.48 | 0.85 | 121.55 | 76.22 | AC-3.2-1 |
| --- | --- | --- | --- | --- | --- |

| NSTX Aux Sys AC Power | 3.50 | 0.80 | 2.80 | 2.10 | AC-3.3-1 |
| --- | --- | --- | --- | --- | --- |

| PPPL House Power (A,B,C,D-sites) | 8.75 | 0.80 | 7.00 | 5.25 | 27 |
| --- | --- | --- | --- | --- | --- |

| Base load between pulses | 13.43 | 0.80 | 10.75 | 8.05 |  |
| --- | --- | --- | --- | --- | --- |

| Pulsed load | 143.48 | 0.85 | 121.55 | 76.22 |  |
| --- | --- | --- | --- | --- | --- |

| Peak load during pulses | 155.69 | 0.84 | 131.35 | 83.57 |  |
| --- | --- | --- | --- | --- | --- |

The following is a description of various details related to the requirements listed in Table AC-3.1-1:

a. Any combination of pulsed load and repetition period with ∫i2(t)dt less than or equal to that described by the nominal loading scenario shall be possible, as long as the repetition period is not less the minimum NSTX repetition period and as long as the peak active and

reactive power demands do not exceed the nominal maximum values given in Table AC-3.1-1.

b. Voltage variations and distortion at PPPL's 138 kV bus, under regular operating conditions shall conform to IEEE 519, "IEEE Guide for Harmonic Control and Reactive Compensation of Static Power Converters".

c. Voltage variations at PPPL's 138 kV bus, under unusual and fault conditions (such as load shed or short circuit) shall be limited to less than +/-10%.

d. Harmonic content of the line current at PPPL's 138 kV bus shall not exceed that of a 12 pulse rectifier, i.e.:

harmonic:  				11th    13th    23rd      25th

rms % of fundamental:      		9         7.5       4.5          4

e. Operation at full rating shall not be restricted to any particular time of day.

f. Experimental power loads from other machines at PPPL shall be assumed inactive or not coincident with NSTX. However, the auxiliary systems loads from other experiments at the laboratory shall be considered coincidental, including those due to D-site.

g. Any restrictions concerning the simultaneous operation of NSTX and the operation of the D-site MG sets shall be explicitly identified.

3.2 Experimental Power Component of Load

Table AC-3.2-1 itemizes and sums the experimental power loads.

Table AC-3.2-1: Experimental Power Loads

|  | MW | Eff | MVA | pf | MW | MVAR | Source | Ref |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| TF (between pulse) |  |  | 1.0 | 0.80 | 0.8 | 0.6 | Q1,Q2 | 87 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| TF (during pulse) |  |  | 0.0 | 0.00 | 0.0 | 0.0 | Q1,Q2 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| PF1 |  |  | 80.0 | 0.85 | 68.0 | 42.1 | S4 | PF-3.2.4-2 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| PF2-8 |  |  | 18.0 | 0.71 | 12.7 | 12.7 | Q1 | PF-3.2.4-2 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| HHFW (per source) | 2.00 | 0.50 | 4.4 | 0.90 | 4.0 | 1.9 | Q6 | 29 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| ECH (per source) | 0.20 | 0.25 | 0.0 | 0.90 | 0.0 | 0.0 | Q6 | 33 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| NBI | 2.00 | 0.45 | 4.9 | 0.90 | 4.4 | 2.2 | Q6 | 37 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| CHI (between pulse) |  |  | 0.04 | 0.90 | 0.03 | 0.02 | Q4 | CHI-3.1-1 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| CHI (during pulse) |  |  | 0.0 | 0.00 | 0.0 | 0.0 | S4 | CHI-3.1-1 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| Baseline | # | MW | MVA | pf | MW | MVAR |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| TF |  |  | 0.0 | 0.00 | 0.0 | 0.0 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| PF1 |  |  | 80.0 | 0.85 | 68.0 | 42.1 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| PF2-8 |  |  | 18.0 | 0.71 | 12.7 | 12.7 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| HHFW | 3.00 | 0.60 | 13.3 | 0.90 | 12.0 | 5.8 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| ECH | 1.00 | 2.00 | 0.0 | 0.00 | 0.0 | 0.0 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| CHI |  |  | 0.0 | 0.00 | 0.0 | 0.0 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| Q1 |  |  | 18.0 | 0.71 | 12.7 | 12.7 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| Q6 |  |  | 13.3 | 0.90 | 12.0 | 5.8 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| S4 |  |  | 80.0 | 0.85 | 68.0 | 42.1 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| Tot Input (between pulse) |  |  | 1.2 | 0.80 | 0.9 | 0.7 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| Tot Input (during pulse) |  |  | 121.9 | 0.84 | 102.0 | 66.8 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| NBI Upgrade | # | MW | MVA | pf | MW | MVAR |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| TF |  |  | 0.0 | 0.0 | 0.0 | 0.0 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| PF1 |  |  | 80.0 | 0.9 | 68.0 | 42.1 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| PF2-8 |  |  | 18.0 | 0.7 | 12.7 | 12.7 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| HHFW | 3.00 | 0.60 | 13.3 | 0.9 | 12.0 | 5.8 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| ECH | 1.00 | 2.00 | 0.0 | 0.0 | 0.0 | 0.0 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| CHI |  |  | 0.0 | 0.0 | 0.0 | 0.0 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| NBI | 4.00 | 8.00 | 19.8 | 0.90 | 17.8 | 8.6 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| Q1 |  |  | 18.0 | 0.71 | 12.7 | 12.7 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| Q6 |  |  | 33.1 | 0.90 | 29.8 | 14.4 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| S4 |  |  | 80.0 | 0.85 | 68.0 | 42.1 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| Tot Input (between pulse) |  |  | 1.2 | 0.80 | 0.9 | 0.7 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| Tot Input (during pulse) |  |  | 143.5 | 0.85 | 121.6 | 76.2 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

The following is a description of various details related to the requirements listed in Table AC-3.2-1:

a. Input power levels given in Table AC-3.2-1 are 110% of required outputs, to account for transformer and line losses.

b. The TF system is assumed powered entirely from the C-site generators during a pulse; the motors are off, and no TF power is derived from the grid.

c. The PF1 load apparent power is based on the product of the maximum no-load DC voltage and maximum DC current. A power factor of 0.85 is assumed.

d. The PF2 through 9 apparent power is based on the sum of the products of the maximum no-load DC voltages and maximum DC currents of the associated power supplies. A power factor of 0.707 is assumed.

e. The ECH power during a pulse is assumed to be provided by an energy storage capacitor bank, charged prior to the pulse. Therefore the power consumption during the pulse is zero.

f. The PF1 (OH) and CHI loads are mutually exclusive. Furthermore (in the CHI sustainment mode) the CHI loads are lower than the OH loads. Therefore the OH loads, and not the CHI loads, are included in the above tables.

g. Any combination of pulsed load and repetition period with ∫i2(t)dt less than or equal to that described by the nominal loading scenario shall be possible, as long as the repetition period is not less than the minimum NSTX repetition period and as long as the peak active and reactive power demands do not exceed the nominal maximum values given in Table AC-3.2.

h. Long Pulse Upgrade loads shall be assumed identical to the NBI Upgrade except that long pulse operation is required.

3.3 Auxiliary Systems Component of Load

Input and output requirements are summarized in Table AC-3.3-1.

Table AC-3.3-1: Auxiliary Power Loads

| Description | MVA | p.f. | MW | MVAR | Ref |
| --- | --- | --- | --- | --- | --- |

| WBS 2 Heating Systems | 0.500 | 0.800 | 0.400 | 0.300 | 41 |
| --- | --- | --- | --- | --- | --- |

| WBS 2 Heating Systems (NBI Upgrade) | 0.500 | 0.800 | 0.400 | 0.300 | 42 |
| --- | --- | --- | --- | --- | --- |

| WBS 3 Auxiliary Systems | 1.000 | 0.800 | 0.800 | 0.600 | 43 |
| --- | --- | --- | --- | --- | --- |

| WBS 4 Plasma Diagnostics | 0.500 | 0.800 | 0.400 | 0.300 | 44 |
| --- | --- | --- | --- | --- | --- |

| WBS 5 Power Systems | 0.500 | 0.800 | 0.400 | 0.300 | 45 |
| --- | --- | --- | --- | --- | --- |

| WBS 6 Central I&C | 0.250 | 0.800 | 0.200 | 0.150 | 46 |
| --- | --- | --- | --- | --- | --- |

| WBS 8 Facilities | 0.750 | 0.800 | 0.600 | 0.450 | 47 |
| --- | --- | --- | --- | --- | --- |

| Total NSTX Aux Sys | 3.500 | 0.800 | 2.800 | 2.100 |  |
| --- | --- | --- | --- | --- | --- |

| Total NSTX Aux Sys (NBI Upgrade) | 3.500 | 0.800 | 2.800 | 2.100 |  |
| --- | --- | --- | --- | --- | --- |

WBS 52 -  Toroidal Field (TF) Power Conversion Requirements

1.0 Functions

a. The TF Power Conversion System shall be designed to provide a constant current in the TF magnets during an NSTX discharge based on a reference current input signal provided in real time.

2.0 Configuration Requirements & Essential Features

a. The TF Power Conversion System shall include all equipment necessary to power the TF coils. This shall include all equipment from the AC input power interface through to the DC bus connections to the magnets, consisting of the C-site MG sets, DC bus, disconnect switches and bus links, and all associated monitoring, control, and protection equipment.

b. Bus links or other means shall be provided in order that the current in the TF magnets can be driven in either direction. However the toroidal field direction shall always be opposite to the plasma current direction. The polarity reversal procedure shall require 4 hours or less [R9]

c. No-load disconnect switches shall be provided to isolate the TF Power Conversion System from the connections to the TF magnets. In addition, no-load grounding switches shall be provided to ground the terminals of the connections to the TF magnets. These switches shall be interlocked with test cell access control [R9].

d. The TF power system equipment shall be equipped with a local control system which shall include provisions for closed loop current control using proportional (P) and integral (I) feedback to effect tracking of reference signals.

e. The TF Power Conversion System shall include protection to avoid the delivery of current which would overheat the TF magnets, assuming that their coolant conditions are nominal [R9].

f. Redundant measurements of TF current shall be provided [R9].

g. The TF power  system  shall be grounded via high resistance connections at the (+) and (-) coil terminals.  A ground fault protection system shall be used in conjunction with the grounding scheme to detect grounds within the TF circuit.

h. The TF power system equipment and bus system external to the test cell shall be totally enclosed so that access can be maintained around the operating equipment without danger to the personnel.

3.0 Performance & Operational Requirements

3.1 Baseline Operation

Basic requirements are summarized in Table TF-3.1-1.

Table TF-3.1-1: TF Requirements

| Parameter | Value | Units | Ref |
| --- | --- | --- | --- |

| Major Radius R | 0.85 | m | 48 |
| --- | --- | --- | --- |

| TF Coil # Turns | 72 | turns | 49 |
| --- | --- | --- | --- |

| TF Coil Inductance | 0.017 | henries | 50 |
| --- | --- | --- | --- |

| Max Allowable Equivalent Square Wave | 6.0 | sec | 51 |
| --- | --- | --- | --- |

| TF Resistance vs. I2T Function C0 | 2.0874E-02 | Ω | 52 |
| --- | --- | --- | --- |

| TF Resistance vs. I2T Function C1 | 3.3314E-12 | Ω/A^2-s | 53 |
| --- | --- | --- | --- |

| TF Resistance vs. I2T Function C2 | 3.6422E-22 | Ω/(A^2-s)^2 | 54 |
| --- | --- | --- | --- |

| TF B - Baseline Pulse | 0.3000 | Tesla | 55 |
| --- | --- | --- | --- |

| TF Flat Top Duration - Baseline Pulse | 5.00 | sec | 56 |
| --- | --- | --- | --- |

| TF Repetition Period - Baseline Pulse | 300.00 | sec | 57 |
| --- | --- | --- | --- |

| TF B - High Field Pulse | 0.6000 | Tesla | 58 |
| --- | --- | --- | --- |

| TF Flat Top Duration - High Field Pulse | 0.60 | sec | 59 |
| --- | --- | --- | --- |

| TF Repetition Period - High Field Pulse | 300.00 | sec | 60 |
| --- | --- | --- | --- |

| TF B - Long Pulse | 0.3200 | Tesla | 61 |
| --- | --- | --- | --- |

| TF Flat Top Duration - Long Pulse | 60.00 | sec | 62 |
| --- | --- | --- | --- |

| TF Repetition Period - Long Pulse | 3600.00 | sec | 63 |
| --- | --- | --- | --- |

| TF Current Measurement Accuracy | 0.5 | % | 64 |
| --- | --- | --- | --- |

| TF Current Control Accuracy | 1 | % | 65 |
| --- | --- | --- | --- |

The following are points of elaboration with regard to Table TF-3.1-1:

a. The Equivalent Square Wave (ESW) is the time duration of a constant current (equal to the current required to produce the required magnetic field) for which the ∫i2(t)dt produces the maximum allowable coil temperature rise under adiabatic conditions. The current waveform in actual operation shall have an ∫i2(t)dt which is less than or equal to that given by the ESW.

b. The TF Resistance vs. ∫i2(t)dt is characterized by a function of the form:

R = C0 + C1 * X + C2 * X2

where:

R 		= total TF coil circuit resistance in ohms

X 		= ∫i2(t)dt in amp2-seconds

C0, C1, C2	= coefficients given in Table TF-1.3-1

c. Current measurement accuracy specification is defined as the absolute value of the difference between the measured value and the actual value as a percentage of the full scale value.

d. The current control accuracy specification corresponds to steady state conditions and is defined as the difference between the measured DC current and the reference current as a percentage of the full scale current, excluding measurement errors.

The derived TF ampacity requirements are summarized in Table TF-3.1-2.

Table TF-3.1-2 TF Ampacity Requirements

| Parameter | Value | Units | Ref |
| --- | --- | --- | --- |

| Baseline Pulse Current | 17791.7 | Amp |  |
| --- | --- | --- | --- |

| Baseline Pulse ESW | 6.0 |  | 51 |
| --- | --- | --- | --- |

| Baseline Pulse ∫i^2dt | 1.90E+09 | amp^2-sec |  |
| --- | --- | --- | --- |

| Baseline Pulse Repetition Period | 300.0 | sec | 57 |
| --- | --- | --- | --- |

| Baseline Pulse Irms | 2516.1 | amps |  |
| --- | --- | --- | --- |

| High Field Pulse Current | 35583.3 | Amp |  |
| --- | --- | --- | --- |

| High Field Pulse ESW | 1.5 |  |  |
| --- | --- | --- | --- |

| High Field Pulse ∫i^2dt | 1.90E+09 | amp^2-sec |  |
| --- | --- | --- | --- |

| High Field Pulse Repetition Period | 300.0 | sec |  |
| --- | --- | --- | --- |

| High Field Pulse Irms | 2516.1 | amps |  |
| --- | --- | --- | --- |

| Baseline Minimum Coil Resistance | 2.0874E-02 | Ω |  |
| --- | --- | --- | --- |

| Baseline Maximum Coil Resistance | 2.8515E-02 | Ω |  |
| --- | --- | --- | --- |

| Energy per Baseline Pulse | 4.53E+07 | Joule |  |
| --- | --- | --- | --- |

| Long Pulse Current | 18977.8 | amps |  |
| --- | --- | --- | --- |

| Long Pulse ESW | 60.0 | sec | 62 |
| --- | --- | --- | --- |

| Long Pulse ∫i^2dt | 2.16E+10 | amp^2-sec |  |
| --- | --- | --- | --- |

| Long Pulse Repetition Period | 3600.0 | sec |  |
| --- | --- | --- | --- |

| Long Pulse Irms | 2450.0 | amps |  |
| --- | --- | --- | --- |

The following are points of elaboration with regard to Table TF-3.1-2:

a. The TF power supply system shall be capable of driving the coil current from zero to full current, regulating the current at the specified flat top value for the specified flat top period, and then driving the current to zero. The ∫i2(t)dt of the resultant waveform shall be within the specified limit.

b. In case of a fault the TF power supply shall shut down in such a way that the maximum ∫i2(t)dt of the pre-fault and post-fault current waveform does not exceed the maximum value given Table TF-1.3-2.

3.1 Upgrades

a. None of the upgrade requirements are imposed on the baseline TF Power Conversion System [R3].

WBS 53 -  Poloidal Field/Ohmic Heating (PF/OH) Requirements

1.0 Functions

a. The PF/OH Power Conversion System shall provide a variable current in the PF and OH magnet circuits  during an NSTX discharge based on a reference current input signal provided in real time [R10].

2.0 Configuration Requirements & Essential Features

a. The PF/OH Power Conversion System shall include all of the equipment necessary to power the PF coils.  This includes all equipment from the primary terminals of the converter transformers through to the DC bus connections to the magnets, consisting of phase controlled thyristor converters, disconnect switches and bus links, and all associated monitoring, and protection equipment.

b. The PF coils shall be connected in series groups in galvanically separate circuits with independent current control as indicated in Table PF-2.0-1 [R11].

Table PF-2.0-1: Galvanically Separate PF Circuits

| PF Circuit | Coil Grouping |
| --- | --- |

| 1 | OH |
| --- | --- |

| 2 | PF1b, upper & lower |
| --- | --- |

| 3 | PF2a, upper & lower |
| --- | --- |

| 4 | PF2b upper |
| --- | --- |

| 5 | PF2b lower |
| --- | --- |

| 6 | PF3a, upper & lower |
| --- | --- |

| 7 | PF3b upper |
| --- | --- |

| 8 | PF3b lower |
| --- | --- |

| 9 | PF4a, PF4b, PF4c, upper & lower |
| --- | --- |

c. All series coil connections indicted in Table PF-2.0-1 shall result in current flow which is equal in magnitude, and in the same φ direction, in the upper and lower coils [R11].

d. All PF circuits except for OH shall be unipolar during a pulse [R10].

e. Bus links shall be provided to permit the connection of the available C-site ESAT building power supplies to the PF2 through PF9 circuits in a variety of configurations.

f. Bus links or other means shall be provided in order that the current in the PF magnets can be driven in either direction. The polarity reversal procedure shall require 4 hours or less [R10].

g. No-load disconnect switches shall be provided to isolate the PF Power System from the connections to the PF magnets. In addition, no-load grounding switches shall be provided to ground the terminals of the connections to the PF magnets. These switches shall be interlocked with test cell access control [R10].

h. Redundant measurements of each PF current shall be provided [R10].

i. The PF Power Conversion System shall include protection to avoid the delivery of current which would overheat the PF magnets, assuming that their coolant conditions are nominal [R10].

3.0 Performance & Operational Requirements

3.1 Description of PF/OH Coils

The PF coils are described by their basic geometry as summarized in Table PF-3.1-1 [R66], and their properties as summarized in Table PF-3.1-2.

Table PF-3.1-1: PF/OH Coil Geometry

| Coil | R (center) | ∆R | Z (center) | ∆Z | Turns | Fill | Cond | Ref |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

|  | (cm) | (cm) | (cm) | (cm) |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| OHa | 12.65 | 4.30 | 55.16 | 110.32 | 290 | 0.7387 | Cu | 66 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| OHb | 12.65 | 4.30 | 159.73 | 98.84 | 88 | 0.8293 | Cu | 66 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| OHc | 17.45 | 4.10 | 156.25 | 94.47 | 88 | 0.7612 | Cu | 66 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| PF1 | 21.75 | 3.30 | 155.89 | 64.56 | 74 | 0.6637 | Cu | 66 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| PF2a | 79.92 | 16.27 | 193.35 | 6.80 | 14 | 0.7363 | Cu | 66 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| PF2b | 79.92 | 16.27 | 185.26 | 6.80 | 14 | 0.7363 | Cu | 66 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| PF3a | 149.45 | 18.64 | 163.35 | 6.80 | 15 | 0.6886 | Cu | 66 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| PF3b | 149.45 | 18.64 | 155.26 | 6.80 | 15 | 0.6886 | Cu | 66 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| PF4a | 178.27 | 6.78 | 72.75 | 6.80 | 5 | 0.6310 | Cu | 66 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| PF4b | 179.46 | 9.15 | 64.66 | 6.80 | 8 | 0.7479 | Cu | 66 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| PF4c | 180.65 | 11.53 | 56.57 | 6.80 | 9 | 0.6682 | Cu | 66 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

Table PF-3.1-2: PF Conductor Properties

| Parameter | Value | Units | Ref |
| --- | --- | --- | --- |

| Resistivity (20C) | 1.724E-06 | Ω-cm | 67 |
| --- | --- | --- | --- |

| Density | 8.9400 | gm/cc | 68 |
| --- | --- | --- | --- |

| Specific Heat | 0.3860 | J/gm-degC | 69 |
| --- | --- | --- | --- |

| Res Temp Coeff | 0.0041 | 1/degC | 70 |
| --- | --- | --- | --- |

| Initial Temp | 20.0 | degC | 71 |
| --- | --- | --- | --- |

Based on the coil grouping given in Table PF-2.0-1, the coil geometry given in Table PF-3.1-1, and the PF conductor properties given in Table PF-3.1-2, the PF circuit 20 C resistances are given in Tables PF-3.1-3 [R75], and the mutual inductance matrix is given in Table PF-3.1-4 [R75].

Table PF-3.1-2: PF Circuit Resistances

| Circuit | Resistance |
| --- | --- |

|  | Ω @ 20C |
| --- | --- |

| PF1 | 8.166E-02 |
| --- | --- |

| PF2 | 1.824E-02 |
| --- | --- |

| PF3 | 4.167E-03 |
| --- | --- |

| PF4 | 2.083E-03 |
| --- | --- |

| PF5 | 2.083E-03 |
| --- | --- |

| PF6 | 8.349E-03 |
| --- | --- |

| PF7 | 4.174E-03 |
| --- | --- |

| PF8 | 4.174E-03 |
| --- | --- |

| PF9 | 1.472E-02 |
| --- | --- |

Table PF-3.1-3: PF Mutual Inductance Matrix (mH)

|  | PF1 | PF2 | PF3 | PF4 | PF5 | PF6 | PF7 | PF8 | PF9 | Plasma |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| PF1 | 12.479 | 2.802 | 0.267 | 0.145 | 0.145 | 0.302 | 0.157 | 0.184 | 0.535 | 1.53E-02 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| PF2 | 2.802 | 2.793 | 0.212 | 0.116 | 0.116 | 0.173 | 0.087 | 0.131 | 0.195 | 2.30E-03 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| PF3 | 0.267 | 0.212 | 1.117 | 0.434 | 0.434 | 0.386 | 0.184 | 0.214 | 0.298 | 2.32E-03 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| PF4 | 0.145 | 0.116 | 0.434 | 0.556 | 0.003 | 0.202 | 0.183 | 0.005 | 0.159 | 1.28E-03 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| PF5 | 0.145 | 0.116 | 0.434 | 0.003 | 0.556 | 0.202 | 0.011 | 0.251 | 0.159 | 1.28E-03 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| PF6 | 0.302 | 0.173 | 0.386 | 0.202 | 0.202 | 2.920 | 1.210 | 0.307 | 1.256 | 8.04E-03 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| PF7 | 0.157 | 0.087 | 0.184 | 0.183 | 0.011 | 1.210 | 1.421 | 0.018 | 0.678 | 4.36E-03 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| PF8 | 0.184 | 0.131 | 0.214 | 0.005 | 0.251 | 0.307 | 0.018 | 0.735 | 0.278 | 2.44E-03 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| PF9 | 0.535 | 0.195 | 0.298 | 0.159 | 0.159 | 1.256 | 0.678 | 0.278 | 8.562 | 3.05E-02 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| Plasma | 0.015 | 0.002 | 0.002 | 0.001 | 0.001 | 0.008 | 0.004 | 0.002 | 0.031 | 9.77E-05 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

3.2 Baseline Operation

3.2.1 Plasma Equilibria Requirements

a. The coil currents in PF circuits 2 through 9 which are required to maintain equilibrium for various plasma conditions (internal inductance (li), aspect ratio (A), elongation (κ), and triangularity (δ)) shall be determined by NSTX project physics. Since the available power supplies are fixed in their number and ampacity, operation of the NSTX machine must conform to the capablity of the existing equipment.

b. The power supplies utilized to power PF circuits 2 through 9 shall be capable of operation at their peak rated current for the full rated NSTX plasma duration (SOD to EOD), with repetition rate in accordance with the rated NSTX duty cycle (section PS-3.1).

c. Provision shall be made to permit the parallel connection of subsets of the available C-site ESAT building power supplies (of identical current/voltage rating) to achieve the maximum possible range of current levels to which PF circuits 2 through 9 can be driven.

3.2.2 Plasma Scenario Requirements

a. The PF1 (OH) power supply shall support plasma current ramp up and ramp down rates of between 0.2 and 0.4 seconds, with a flat top time up to 0.5 seconds, while limiting the ∫i2(t)dt heating of the OH coil to < 100C. In terms of required OH power supply voltage

and ∫i2(t)dt, the 0.4 second case is the most severe. The required current and voltage waveforms for this case are depicted in figures PF-3.2-1 and PF-3.2-2. The voltage waveform is based on a constant coil resistance at 100C, with mutual coupling to a 1.0MA plasma, but without mutual coupling to the other PF circuits.

Figure PF-3.2-1: OH Current Waveform, 0.4s Ramp Interval

Figure PF-3.2-2: OH Voltage Waveform, 0.4s Ramp Interval

b. The plasma ramp up and ramp down times available during NSTX operation may be limited in some cases by the voltage available from the C-site ESAT building power supplies.

c. Provision shall be made to permit the series connection of subsets of the available C-site ESAT building power supplies to achieve the maximum possible range of voltage levels with which PF circuits 2 through 9 can be driven.

d. The PF ampacity requirements are summarized in Table PF-3.2-1 [R75].

Table PF-3.2-1: PF Ampacity Requirements

| Circuit | Max Curr | Max ESW | Max ∫i^2(t)dt | Max Irms |
| --- | --- | --- | --- | --- |

|  | kA | sec | A^2-sec | kA |
| --- | --- | --- | --- | --- |

| PF1 | 20.0 | 0.50 | 2.000E+08 | 0.577 |
| --- | --- | --- | --- | --- |

| PF2 | 10.0 | 5.00 | 5.000E+08 | 1.291 |
| --- | --- | --- | --- | --- |

| PF3 | 20.0 | 5.00 | 2.000E+09 | 2.582 |
| --- | --- | --- | --- | --- |

| PF4 | 20.0 | 5.00 | 2.000E+09 | 2.582 |
| --- | --- | --- | --- | --- |

| PF5 | 20.0 | 5.00 | 2.000E+09 | 2.582 |
| --- | --- | --- | --- | --- |

| PF6 | 20.0 | 5.00 | 2.000E+09 | 2.582 |
| --- | --- | --- | --- | --- |

| PF7 | 20.0 | 5.00 | 2.000E+09 | 2.582 |
| --- | --- | --- | --- | --- |

| PF8 | 20.0 | 5.00 | 2.000E+09 | 2.582 |
| --- | --- | --- | --- | --- |

| PF9 | 20.0 | 5.00 | 2.000E+09 | 2.582 |
| --- | --- | --- | --- | --- |

3.2.3 Other Requirements

PF/OH Current measurement and control accuracy requirements are given in Table PF-3.2-2.

Table PF-3.2-2: PF Measurement and Control Accuracy Requirements

| Parameter | Value | Units | Ref |
| --- | --- | --- | --- |

| Current Measurement Accuracy | 0.5 | % | 78 |
| --- | --- | --- | --- |

| Current Control Accuracy | 0.5 | % | 79 |
| --- | --- | --- | --- |

a. Current measurement accuracy specification is defined as the absolute value of the difference between the measured value and the actual value as a percentage of the full scale value.

b. The current control accuracy specification corresponds to steady state conditions and is defined as the difference between the measured DC current and the reference current as a percentage of the full scale current, excluding measurement errors.

3.2 Upgrades

a. None of the upgrade requirements are imposed on the baseline PF Power Conversion System [R3].

WBS 54 -  CHI Power Conversion System Requirements

1.0 Functions

a. The function of the CHI power system (WBS 54) is to energize the CHI electrodes and impart a poloidal component of current flow which, due to the influence of the toroidal field, results in a toroidal component of plasma current. The power supply consists of an energy storage capacitor bank with associated charge/discharge equipment along with provision for an upgrade to include an additional power supply to provide current drive after the capacitor bank discharge.

2.0 Configuration Requirements & Essential Features

a. CHI Power System shall be designed to provide a capacitor bank discharge.

b. Provision shall be made for an upgrade to include a power supply drive following the capacitor bank discharge [R13]. The power supply shall be a one-quadrant thyristor converter (+V, +I) controllable in either of two modes, namely:

- closed loop current control against a time varying reference current

- open loop voltage control against a time varying reference voltage

c. Bus links or other means shall be provided in order that the current in the CHI circuit can be driven in either direction. The polarity reversal procedure shall require 4 hours or less [R13].

d. No-load disconnect switches shall be provided to isolate the CHI Power System from the connections to the CHI electrodes. In addition, no-load grounding switches shall be provided to ground the terminals of the connections to the CHI electrodes. These switched shall be interlocked with test cell access control [R13].

3.0 Performance & Operational Requirements

3.1 Baseline Operation

CHI performance requirements are given in Table CHI-3.1-1.

Table CHI-3.1-1 CHI Power System Requirements

| Parameter | Value | Units | Ref |
| --- | --- | --- | --- |

| CHI Capacitor Energy | 2.00E+06 | Joule | 80 |
| --- | --- | --- | --- |

| CHI Ip/Ichi Ratio | 1.00E+01 |  | 81 |
| --- | --- | --- | --- |

| CHI Capacitor Driven Ip | 5.00E+05 | Amp | 82 |
| --- | --- | --- | --- |

| CHI Power Supply Driven Ip | 2.00E+05 | Amp | 83 |
| --- | --- | --- | --- |

| CHI Power Supply Driven Power | 1.50E+07 | Watt | 84 |
| --- | --- | --- | --- |

| CHI Current Measurement Accuracy | 0.5 | % | 85 |
| --- | --- | --- | --- |

| CHI Current Control Accuracy | 0.5 | % | 86 |
| --- | --- | --- | --- |

The results of an analysis of the CHI requirements, based on a simple LRC circuit, and assuming the use of two TFTR capacitor banks, is given in Table CHI 3.1-2.

Table CHI 3.1-1 CHI Power System Requirements Analysis

| Parameter | Value | Units | Ref |
| --- | --- | --- | --- |

| Ip | 5.00E+05 | amp |  |
| --- | --- | --- | --- |

| Ip/Ichi | 10 |  |  |
| --- | --- | --- | --- |

| Ichi | 50000 | amp |  |
| --- | --- | --- | --- |

| Lp | 1.00E-07 | henry |  |
| --- | --- | --- | --- |

| Wp | 12500 | joule |  |
| --- | --- | --- | --- |

| Cbank | 9.90E-03 | farad |  |
| --- | --- | --- | --- |

| Lbank | 8.80E-04 | henry |  |
| --- | --- | --- | --- |

| Nbank | 2 |  |  |
| --- | --- | --- | --- |

| Lchi | 4.50E-04 | henry |  |
| --- | --- | --- | --- |

| Cchi | 1.98E-02 | farad |  |
| --- | --- | --- | --- |

| Rchi | 0.0375 | ohm |  |
| --- | --- | --- | --- |

| Omega0 | 332.4 | radians/sec |  |
| --- | --- | --- | --- |

| Vchi | 9037.0 | volt |  |
| --- | --- | --- | --- |

| Prospective Ipeak | 60413.9 | amp |  |
| --- | --- | --- | --- |

| Ipps | 200000 | amp |  |
| --- | --- | --- | --- |

| Ichips | 20000 | amp |  |
| --- | --- | --- | --- |

| Pchips | 1.50E+07 | watt |  |
| --- | --- | --- | --- |

| Vchips | 750 | volt |  |
| --- | --- | --- | --- |

| Cap Dschg ∫i^2(t)dt | 7.58E+06 | amp^2-sec |  |
| --- | --- | --- | --- |

| Cap Dschg Energy | 7.58E+07 | joule |  |
| --- | --- | --- | --- |

| PS Duration | 5.00E+00 | sec | 21 |
| --- | --- | --- | --- |

| Rep Period | 3.00E+02 | sec | 22 |
| --- | --- | --- | --- |

| Cap rms | 159.0 | amp |  |
| --- | --- | --- | --- |

| PS rms | 2582.0 | amp |  |
| --- | --- | --- | --- |

| Circuit rms | 2586.9 | amp |  |
| --- | --- | --- | --- |

| Cap Charge Time | 60 | sec |  |
| --- | --- | --- | --- |

| Cap Charge Power per Bank | 16666.67 | watt |  |
| --- | --- | --- | --- |

| Total Cap Charge Power | 33333.33 | watt |  |
| --- | --- | --- | --- |

The capacitor discharge and transition to power supply current drive waveform is given in figure CHI 3.1-1.

Figure CHI 3.1-1:  CHI Capacitor Current Discharge Waveform

The following is a description of various details related to the requirements:

a. The CHI power system shall be capable of operation with any set of waveforms and duty cycles characterized by peak current and ∫i2(t)dt within the maximum allowable values.

b. For the power supply upgrade, closed loop current control shall utilize both proportional (P) and integral (I) terms in the control law. The current control error specification corresponds to steady state conditions and is defined as the difference between the measured DC current and the reference current as a percentage of the full scale current, excluding measurement errors.

c. The required current control accuracy shall be achievable with a load of constant inductance and resistance as specified.

d. Voltage measurements shall be made from both bus terminals to ground. Frequency response shall be DC to 1MHz minimum.

e. Current measurement error specification is defined as the difference between the measured value and the actual value as a percentage of the full scale value.

f. The CHI circuit  shall be grounded via the vacuum vessel ground. A ground fault protection system shall be used in conjunction with the grounding scheme to detect grounds within the CHI circuit.

g. The CHI power conversion equipment and bus system shall be totally enclosed so that access can be maintained around the operating equipment without danger to the personnel.

3.2 Upgrades

a. See description of power supply performance requirements in section 3.1. .

| R | Description | Value | Units | Reference |
| --- | --- | --- | --- | --- |

| 1 | Location of NSTX | na | na | GRD sec 1.1.1 |
| --- | --- | --- | --- | --- |

| 2 | Req'ts for compatibility with PBX | na | na | GRD sec 1.6 |
| --- | --- | --- | --- | --- |

| 3 | Baseline and Upgrade Req'ts | na | na | GRD sec 1.1.2 |
| --- | --- | --- | --- | --- |

| 4 | NSTX Scenario Descriptions | na | na | GRD sec 2.1.2.1 |
| --- | --- | --- | --- | --- |

| 5 | NSTX Upgrade Requirements | na | na | GRD sec 2.1.3 |
| --- | --- | --- | --- | --- |

| 6 | NSTX Operating Lifetime Requirements | na | na | GRD sec 2.1.2.3 |
| --- | --- | --- | --- | --- |

| 7 | Req'ts for Non-Simultaneous Pulsing | na | na | GRD sec 1.6.1 |
| --- | --- | --- | --- | --- |

| 8 | PPPL AC Power System Equivalent Circuit | na | na | "Analysis of TPX Pulsing of Utility Grid", TPX Memo 41-940502-PPPL/CNeumeyer-01 |
| --- | --- | --- | --- | --- |

| 9 | TF Configuation & Feature Req'ts | na | na | GRD sec 1.6.2 |
| --- | --- | --- | --- | --- |

| 10 | PF/OH Configuation & Feature Req'ts | na | na | GRD sec 1.6.3 |
| --- | --- | --- | --- | --- |

| 11 | PF Circuit Definition | na | na | GRD sec 1.2.3.1 |
| --- | --- | --- | --- | --- |

| 12 | CHI Configuration & Feature Req'ts | na | na | GRD sec 1.6.4 |
| --- | --- | --- | --- | --- |

| 13 |  |  |  |  |
| --- | --- | --- | --- | --- |

| 14 |  |  |  |  |
| --- | --- | --- | --- | --- |

| 15 |  |  |  |  |
| --- | --- | --- | --- | --- |

| 16 |  |  |  |  |
| --- | --- | --- | --- | --- |

| 17 |  |  |  |  |
| --- | --- | --- | --- | --- |

| 18 |  |  |  |  |
| --- | --- | --- | --- | --- |

| 19 | Inductive Maximum Pulse Duration | 0.50 | sec | GRD sec 2.1.2.1.1 |
| --- | --- | --- | --- | --- |

| 20 | Inductive minimum Repetition period | 600.00 | sec | GRD sec 2.1.2.3.a |
| --- | --- | --- | --- | --- |

| 21 | Non-Inductive Maximum Pulse Duration | 5.00 | sec | GRD sec 2.1.2.1.2 |
| --- | --- | --- | --- | --- |

| 22 | Non-Inductive Minimum Repetition Period | 300.00 | sec | GRD sec 2.1.2.3.b |
| --- | --- | --- | --- | --- |

| 23 | Upgrade maximum Pulse duration | 60.00 | sec | GRD sec 2.1.3.2.a |
| --- | --- | --- | --- | --- |

| 24 | Upgrade minimum Repetition period | 3600.00 | sec | GRD sec 2.1.3.2.a |
| --- | --- | --- | --- | --- |

| 25 | Operating lifetime | 25.00 | years | GRD sec 2.1.2.3.c |
| --- | --- | --- | --- | --- |

| 26 | Baseline number of pulses | 130000.00 | pulses | GRD sec 2.1.2.3.d |
| --- | --- | --- | --- | --- |

| 27 | PPPL A,B,C,D site House Power | 8.75 | MVA |  |
| --- | --- | --- | --- | --- |

| 28 | PPPL A,B,C,D site House Power Factor | 0.80 | p.u. |  |
| --- | --- | --- | --- | --- |

| 29 | HHFW Power per Source to Plasma | 2.00 | MW |  |
| --- | --- | --- | --- | --- |

| 30 | HHFW Efficiency | 0.50 | p.u. |  |
| --- | --- | --- | --- | --- |

| 31 | HHFW Power Factor | 0.90 | p.u. |  |
| --- | --- | --- | --- | --- |

| 32 | HHFW Number of Sources | 3.00 | sources |  |
| --- | --- | --- | --- | --- |

| 33 | ECH Power per Source to Plasma | 0.20 | MW |  |
| --- | --- | --- | --- | --- |

| 34 | ECH Efficiency | 0.25 | p.u. |  |
| --- | --- | --- | --- | --- |

| 35 | ECH Power Factor | 0.90 | p.u. |  |
| --- | --- | --- | --- | --- |

| 36 | ECH Number of Sources | 1.00 | sources |  |
| --- | --- | --- | --- | --- |

| 37 | NBI Power per Source to Plasma | 2.00 | MW |  |
| --- | --- | --- | --- | --- |

| 38 | NBI Efficiency | 0.45 | p.u. |  |
| --- | --- | --- | --- | --- |

| 39 | NBI Power Factor | 0.90 | p.u. |  |
| --- | --- | --- | --- | --- |

| 40 | NBI Number of Sources (Upgrade) | 4.00 | sources |  |
| --- | --- | --- | --- | --- |

| 41 | WBS 2 Heating Sys Aux AC Power | 0.50 | MVA |  |
| --- | --- | --- | --- | --- |

| 42 | WBS 2 Heating Sys Aux AC Power (Upgrade) | 0.50 | MVA |  |
| --- | --- | --- | --- | --- |

| 43 | WBS 3 Auxiliary Sys Aux AC Power | 1.00 | MVA |  |
| --- | --- | --- | --- | --- |

| 44 | WBS 4 Diagnostics Aux AC Power | 0.50 | MVA |  |
| --- | --- | --- | --- | --- |

| 45 | WBS 5 Power Systems Aux AC Power | 0.50 | MVA |  |
| --- | --- | --- | --- | --- |

| 46 | WBS 6 Central I&C Aux AC Power | 0.25 | MVA |  |
| --- | --- | --- | --- | --- |

| 47 | WBS 8 Facilities Aux AC Power | 0.75 | MVA |  |
| --- | --- | --- | --- | --- |

| 48 | Major Radius R | 0.85 | m | GRD sec 2.1.1.b |
| --- | --- | --- | --- | --- |

| 49 | TF Coil # Turns | 72 | turns | TF Coils Spreadsheet |
| --- | --- | --- | --- | --- |

| 50 | TF Coil Inductance | 0.017 | henries | TF Coils Spreadsheet |
| --- | --- | --- | --- | --- |

| 51 | Max Allowable Equivalent Square Wave | 6.0 | sec | TF Coils Spreadsheet |
| --- | --- | --- | --- | --- |

| 52 | TF Resistance vs. I2T Function C0 | 2.0874E-02 | Ω | "TF Resistance vs. I2T",13-960418-AWB-01 |
| --- | --- | --- | --- | --- |

| 53 | TF Resistance vs. I2T Function C1 | 3.3314E-12 | Ω/A^2-s | ditto |
| --- | --- | --- | --- | --- |

| 54 | TF Resistance vs. I2T Function C2 | 3.6422E-22 | Ω/(A^2-s)^2 | ditto |
| --- | --- | --- | --- | --- |

| 55 | TF B - Baseline Pulse | 0.3000 | Tesla | GRD sec 2.1.2.2.b |
| --- | --- | --- | --- | --- |

| 56 | TF Flat Top Duration - Baseline Pulse | 5.00 | sec | GRD sec 2.1.2.2.a |
| --- | --- | --- | --- | --- |

| 57 | TF Repetition Period - Baseline Pulse | 300.00 | sec | GRD sec 2.1.2.3.b |
| --- | --- | --- | --- | --- |

| 58 | TF B - High Field Pulse | 0.6000 | Tesla | GRD sec 2.1.2.2.b |
| --- | --- | --- | --- | --- |

| 59 | TF Flat Top Duration - High Field Pulse | 0.60 | sec | GRD sec 2.1.2.2.b |
| --- | --- | --- | --- | --- |

| 60 | TF Repetition Period - High Field Pulse | 300.00 | sec | GRD sec 2.1.2.3.b |
| --- | --- | --- | --- | --- |

| 61 | TF B - Long Pulse | 0.3000 | Tesla |  |
| --- | --- | --- | --- | --- |

| 62 | TF Flat Top Duration - Long Pulse | 60.00 | sec |  |
| --- | --- | --- | --- | --- |

| 63 | TF Repetition Period - Long Pulse | 3600.00 | sec | GRD sec 2.1.3.2.a |
| --- | --- | --- | --- | --- |

| 64 | TF Current Measurement Accuracy | 0.5 | % |  |
| --- | --- | --- | --- | --- |

| 65 | TF Current Control Accuracy | 1 | % |  |
| --- | --- | --- | --- | --- |

| 66 | PF Geometry Description | na |  | PF Coils Spreadsheet |
| --- | --- | --- | --- | --- |

| 67 | Copper 20C Resistivity | 1.7240E-06 | Ω-cm | PF Coils Spreadsheet |
| --- | --- | --- | --- | --- |

| 68 | Copper Density | 8.94 | gm/cc | PF Coils Spreadsheet |
| --- | --- | --- | --- | --- |

| 69 | Copper Specific Heat | 0.386 | J/gm-degC | PF Coils Spreadsheet |
| --- | --- | --- | --- | --- |

| 70 | Copper Resistance Temperature Coeff | 0.0041 | 1/degC | PF Coils Spreadsheet |
| --- | --- | --- | --- | --- |

| 71 | Inlet Water Temperature | 20 | C | PF Coils Spreadsheet |
| --- | --- | --- | --- | --- |

| 72 | Copper G vs. T | na |  |  |
| --- | --- | --- | --- | --- |

| 73 | Copper T vs. G | na |  |  |
| --- | --- | --- | --- | --- |

| 74 | Copper H vs. T | na |  |  |
| --- | --- | --- | --- | --- |

| 75 | PF Coil Description | na |  | PF Coils Spreadsheet |
| --- | --- | --- | --- | --- |

| 76 | Plasma Equilbria PF Current Distributions | na |  |  |
| --- | --- | --- | --- | --- |

| 77 | PF Scenario Analysis | na |  |  |
| --- | --- | --- | --- | --- |

| 78 | PF Current Measurement Accuracy | 0.5 | % |  |
| --- | --- | --- | --- | --- |

| 79 | PF Current Control Accuracy | 0.5 | % |  |
| --- | --- | --- | --- | --- |

| 80 | CHI Capacitor Energy | 2.00E+06 | Joule | 54-960520-CLN-01, "Assumptions Concerning CHI PS Requirements" |
| --- | --- | --- | --- | --- |

| 81 | CHI Ip/Ichi Ratio | 1.00E+01 |  | GRD sec 2.2.2 |
| --- | --- | --- | --- | --- |

| 82 | CHI Capacitor Driven Ip | 5.00E+05 | Amp | GRD sec 2.2.2 |
| --- | --- | --- | --- | --- |

| 83 | CHI Power Supply Driven Ip | 2.00E+05 | Amp | GRD sec 2.2.2 |
| --- | --- | --- | --- | --- |

| 84 | CHI Power Supply Driven Power | 1.50E+07 | Watt | GRD sec 2.2.2 |
| --- | --- | --- | --- | --- |

| 85 | CHI Current Measurement Accuracy | 5.00E-01 | % |  |
| --- | --- | --- | --- | --- |

| 86 | CHI Current Control Accuracy | 0.5 | % |  |
| --- | --- | --- | --- | --- |

| 87 | C-Site MG Idling Power per Shaft | 0.83 | MW |  |
| --- | --- | --- | --- | --- |

| 88 |  |  |  |  |
| --- | --- | --- | --- | --- |