National Spherical Tokamak Experiment

NSTX

SYSTEM REQUIREMENTS DOCUMENT

POWER SYSTEMS

NSTX-SRD-5X-019

Revision 0

May 7, 1996

________________________________

Charles Neumeyer

WBS 5 Manager,

NSTX Project Engineering Manager

________________________________

Masa Ono

NSTX Project Manager

| Revision | Date | TRB | Description of Change |
| --- | --- | --- | --- |

Introduction	1

General Power System Requirements	2

1.0 Functions	2

2.0 Configuration Requirements & Essential Features	2

3.0 Performance & Operational Requirements	2

3.1 Baseline Operation	2

3.2 Upgrades	3

3.3 Pulse Repetition Period & Operating Life	3

AC Power System Requirements	5

1.0 Functions	5

1.1 Specific Functions of the Experimental AC Power System	5

1.2 Specific Functions of the Auxiliary Systems AC Power System	5

2.0 Configuration Requirements & Essential Features	6

3.0 Performance & Operational Requirements	7

3.1 Composite AC Power Load	7

3.2 Experimental Power Component of Load	8

3.3 Auxiliary Systems Component of Load	10

Toroidal Field (TF) Power Conversion Requirements	11

1.0 Functions	11

2.0 Configuration Requirements & Essential Features	11

3.0 Performance & Operational Requirements	11

3.1 Baseline Operation	11

3.1 Upgrades	13

Poloidal Field/Ohmic Heating (PF/OH) Requirements	14

1.0 Functions	14

2.0 Configuration Requirements & Essential Features	14

3.0 Performance & Operational Requirements	15

3.1 Description of PF/OH Coils	15

3.2 Baseline Operation	16

3.2.1 PF Equilibria Requirements	16

3.2.2 Current Requirements	17

3.2.5 Other Requirements	19

3.2 Upgrades	20

CHI Power Conversion System Requirements	21

1.0 Functions	21

2.0 Configuration Requirements & Essential Features	21

3.0 Performance & Operational Requirements	21

3.1 Baseline Operation	21

3.2 Upgrades	22

List of Tables

PS-3.1-1: Inductive Pulse Duty Cycle	3

PS-3.1-2: Non-Inductive Pulse Duty Cycle	3

PS-3.1-1: Upgrade NSTX Duty Cycle	3

AC-3.1-1: Composite AC Input Power Requirements	7

AC-3.2-1: Experimental Power Loads	8

AC-3.3-1: Auxiliary Power Loads	10

TF-1.3.-1: TF Requirements	11

TF-1.3.-2 TF Ampacity Requirements	11

PF-2.0-1: Galvanically Separate PF Circuits	14

PF-3.1-1: PF/OH Coil Geometry	15

PF-3.1-2: PF Conductor Properties	15

PF-3.1-2: PF Circuit Resistances	15

PF-3.1-3: PF Mutual Inductance Matrix (mH)	15

PF-3.2.1-1: PF Equilibria Current Distributions	16

PF-3.2.2-1: PF Ampacity Requirements	17

PF-3.2.3-1: PF Ramp and Flat Top Times (sec)	17

PF-3.2.3-2: PF Scenario Voltage, Current, ∫i2(t)dt, Loss,Temperature	18

PF-3.2.4-1: PF Power Supply Assignments	18

PF-3.2.4-2: Active and Reactive Power Maximums	18

PF-3.2.5-1: PF Measurement and Control Accuracy Requirements	19

CHI 3.1-1 CHI Power System Requirements	21

List of FIGURES

AC-2.2.1-1: Equivalent Circuit for Utility Grid Interface	6

PF-3.2-1: OH Current Waveform	17

APPENDIX

LIST OF REFERENCES

Introduction

This System Requirements Document (SRD) defines the requirements and design of the Power Systems (WBS 5X) of the National Spherical Tokamak Experiment (NSTX).

A general section covers information which is relevant to the entire WBS element. Individual  subelements of the WBS Sample work scope are covered in separate sections, namely:

• WBS 51 AC Power Systems

• WBS 52 Toroidal Field (TF) Power Conversion System

• WBS 53 Poloidal Field/Ohmic Heating (PF/OH) Power Conversion System

• WBS 54 Coaxial Helicity Injection (CHI) Power Conversion System

Figures and Tables are numbered in format X-Y-Z where X=section (i.e. section abbreviation, e.g. PS for Power System), Y=paragraph number, and Z= sequence number within that paragraph.

References to the requirements identified herein are cited in the body of the document using serial numbers preceded by an "R" and are listed in the Appendix.

WBS 5X -  General Power System Requirements

1.0 Functions

The Power Systems WBS element is required to supply and deliver all electrical power to equipment associated with the NSTX.

2.0 Configuration Requirements & Essential Features

a. The NSTX machine shall be installed at the PPPL C-site C-cell (formerly occupied by the Princeton Large Torus (PLT)) [R1]. The C-site power supply resources shall be utilized to the maximum extent for NSTX operation [R2].

b. Transfer switches shall be provided to allow the shared usage of power supplies which serve both NSTX and PBX-M [R2].

c. Controls and interlocks shall be designed to accommodate shared usage between NSTX and PBX-M [R2].

3.0 Performance & Operational Requirements

a. The baseline design of NSTX shall not preclude the possibility of the upgrades, and shall facilitate the upgrades whenever possible and cost effective. However, for the Power Systems, none of the upgrade features are required to be incorporated in the baseline design of NSTX [R3].

b. The anticipated upgrades include the following [R3]:

• addition of neutral beam injection (NBI)

• long pulse operation (with center stack replacement)

3.1 Baseline Operation

Baseline:

• Pulsed operation with four basic scenarios, namely [R4]:

I. Inductive w/Natural Divertor, 0.5 second flat top

II. Non-Inductive w/Natural Divertor, 5.0 second flat top

III. Non-Inductive w/Double Null (DN) X-point Divertor, 5.0 second flat top

IV. Non-Inductive w/Single Null (SN) X-point Divertor, 5.0 second flat top

• The basic duty cycle of the inductive scenario (Scenario I) is defined in Table PS-3.1-1:

Table PS-3.1-1: Inductive Pulse Duty Cycle

| Parameter | Value | Units | Ref |
| --- | --- | --- | --- |

| Inductive Maximum Pulse Length | 0.5 | sec | 19 |
| --- | --- | --- | --- |

| Inductive Minimum Repetition Period | 600.0 | sec | 20 |
| --- | --- | --- | --- |

• The basic duty cycle of the non-inductive scenarios (Scenario II, III, and IV) is defined in Table PS-3.1-2:

Table PS-3.1-2: Non-Inductive Pulse Duty Cycle

| Parameter | Value | Units | Ref |
| --- | --- | --- | --- |

| Non-Inductive Maximum Pulse Length | 5.0 | sec | 21 |
| --- | --- | --- | --- |

| Non-Inductive Minimum Repetition Period | 300.0 | sec | 22 |
| --- | --- | --- | --- |

• Baseline Heating and Current Drive (H&CD) mix is as follows:

- High Harmonic Fast Wave Current Drive (HHFW)

- Coaxial Helicity Injection (CHI)

- Electron Cyclotron Heating (ECH)

3.2 Upgrades

3.2.1 Neutral Beam Injection (NBI) Upgrade [R5]

a. The Power Systems design shall consider an upgrade which would place the four existing PBX-M sources on NSTX.

b. The baseline design for the Power Systems shall identify an upgrade path for the neutral beam upgrade.

3.2.2 Long Pulse Upgrade [R5]

a. The Power Systems design shall consider an upgrade which would remove the baseline TF and OH magnets, and place a new TF magnet in the center stack. The NSTX plasma pulse length shall be assumed to be 60 seconds for this upgrade.

b. The baseline design for the Power Systems shall identify an upgrade path for the long pulse operation. The assumed repetition period shall be as indicated in Table PS-3.2-1, which would (at the same pulse current magnitude as the baseline) result in the same rms current as the baseline.

Table PS-3.1-1: Upgrade NSTX Duty Cycle

| Parameter | Value | Units | Ref |
| --- | --- | --- | --- |

| Upgrade Maximum Pulse Length | 60.0 | sec | 23 |
| --- | --- | --- | --- |

| Upgrade Minimum Repetition Period | 72000.0 | sec | 24 |
| --- | --- | --- | --- |

3.3 Pulse Repetition Period & Operating Life

a. The baseline Power Systems shall be designed to produce a maximum of 100 pulses per 24 hour period [R6]

b. The Power Systems shall be designed to operate for a period of 10 years [R6].

c. NSTX operation shall be assumed to consist of 100 pulses per day, 5 days per week, 3 weeks per month, 9 months per year, for 10 years (total of 135,000 pulses). Non-operating times are available for maintenance [R6].

WBS 51 -  AC Power System Requirements

The AC Power System WBS Element (WBS 51) is divided into two major subelements, namely the Experimental AC Power System (WBS 511, which includes all loads due to TF, PF,  and H&CD systems) and the Auxiliary Systems AC Power System (WBS 512, which includes all NSTX auxiliary or "house" power demands).

1.0 Functions

a. The function of the AC Power System is to provide the source of all electric power required for the NSTX facility.  The AC Power System must establish the connection between the PPPL facility and the local utility network in a fashion which permits the pulsed loading required by the NSTX experiment while maintaining a power source of suitable quality for existing house loads.

b. Experimental operation of the NSTX facility shall not be coincident with the operation of other major machines at PPPL (TFTR, PBX-M). Provision shall be included to prevent simultaneous operation to the extent that limits on power delivery to PPPL could be exceeded [R7].

1.1 Specific Functions of the Experimental AC Power System

The specific functions of the Experimental AC Power System include:

a. Delivery of power to C-Site 4.16kV Q1, Q2, and Q6 bus, from secondary AC 	terminals of XQT-1 and XQT-2 to Q buses.

b. Delivery of power to C-Site 13.8kV S bus from secondary terminals of

XST-2 to S bus.

c. AC distribution from Q1 bus to the C-site MG equipment

d. AC distribution from Q1 bus to ESAT building rectifier equipment via

Q1-B5 feeder.

e. AC distribution from Q6 bus to H&CD converter transformer primary AC input 	terminals.

f. AC distribution from S bus to OH converter transformer primary terminals

1.2 Specific Functions of the Auxiliary Systems AC Power System

The specific functions of the Auxiliary Systems AC Power System include:

a.  All auxiliary system AC distribution at C-Site pertaining to the NSTX operations, from Q3 and Q4  bus to points of utilization at 4.16kV, 480V, 208V, and 120VAC levels.

c. Standby power diesel generator and all associated equipment.

d. UPS systems and all associated equipment.

2.0 Configuration Requirements & Essential Features

a. All input power shall be derived from the 138kV service incoming to the laboratory.

b. The electrical utility service to the Princeton Plasma Physics Laboratory (PPPL) site is a 138 kV transmission line thermally rated at 600 Amp steady state (equivalent to roughly 140 MVA). Present agreements with the local utility, Public Service Electric and Gas (PSE&G) permit PPPL to take a 120 MVA dynamic load without phase correction.

c. The limitation on pulsed loading of the utility service is determined by the regulatory requirements regarding the voltage variation experienced by other customers as a result of the pulsed load. The utility considers a +/-1% variation at the nearest point of connection to other customers to be acceptable.

d. PPPL's pulsing affects other PPPL's loads which derive power from the 138kV system as well, some of which (such as computer systems) are voltage sensitive. For that reason the dynamic voltage variation at PPPL's 138 kV bus (on pulsing) shall be held to +/-3% or better. The composite loads imposed by NSTX and the remainder of PPPL need to be accommodated, as well as fault transients due to short circuits, load sheds etc.

e. The equivalent circuit given in Figure AC-1-1 shall be utilized for voltage drop and short circuit calculations [R8].

Figure AC-2.2.1-1: Equivalent Circuit for Utility Grid Interface

g. All Auxiliary Power Systems loads shall nominally be powered from the utility power source via XQT-1 and distributed via buses Q3 and Q4.

h. Standard Auxiliary Power Systems services shall be as follows:

• Service voltages (3-phase)		13.8kV, 4.16kV, 480V, 208V

• Service voltages (single phase) 	120V

i. A subset of the Auxiliary Power Systems loads require automatic transfer to the standby (diesel generator) power source in the event of a loss of site power from the 138kV service.

j. A subset of the Auxiliary Power Systems loads require uninterruptable power supplies (UPS).

3.0 Performance & Operational Requirements

3.1 Composite AC Power Load

Table AC-3.1-1 describes the requirements for total (composite) input power, as measured at the 138kV utility interface with PPPL.

Table AC-3.1-1: Composite AC Input Power Requirements

| Load | MVA | p.f | MW | MVAR | Ref |
| --- | --- | --- | --- | --- | --- |

| Baseline |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |

| NSTX Exp AC Power (between pulses) | 0.00 | 0.00 | 0.00 | 0.00 | AC-3.2-1 |
| --- | --- | --- | --- | --- | --- |

| NSTX Exp AC Power (during pulses) | 107.70 | 0.92 | 98.88 | 42.68 | AC-3.2-1 |
| --- | --- | --- | --- | --- | --- |

| NSTX Aux Sys AC Power | 3.50 | 0.80 | 2.80 | 2.10 | AC-3.3-1 |
| --- | --- | --- | --- | --- | --- |

| PPPL House Power (A,B,C,D-sites) | 8.75 | 0.80 | 7.00 | 5.25 | 27 |
| --- | --- | --- | --- | --- | --- |

| Base load between pulses | 12.25 | 0.80 | 9.80 | 7.35 |  |
| --- | --- | --- | --- | --- | --- |

| Pulsed load | 107.70 | 0.92 | 98.88 | 42.68 |  |
| --- | --- | --- | --- | --- | --- |

| Peak load during pulses | 119.64 | 0.91 | 108.68 | 50.03 |  |
| --- | --- | --- | --- | --- | --- |

| NBI Upgrade |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |

| NSTX Exp AC Power (between pulses) | 0.00 | 0.00 | 0.00 | 0.00 | AC-3.2-1 |
| --- | --- | --- | --- | --- | --- |

| NSTX Exp AC Power (during pulses) | 136.41 | 0.91 | 123.93 | 57.01 | AC-3.2-1 |
| --- | --- | --- | --- | --- | --- |

| NSTX Aux Sys AC Power | 3.50 | 0.80 | 2.80 | 2.10 | AC-3.3-1 |
| --- | --- | --- | --- | --- | --- |

| PPPL House Power (A,B,C,D-sites) | 8.75 | 0.80 | 7.00 | 5.25 | 27 |
| --- | --- | --- | --- | --- | --- |

| Base load between pulses | 12.25 | 0.80 | 9.80 | 7.35 |  |
| --- | --- | --- | --- | --- | --- |

| Pulsed load | 136.41 | 0.91 | 123.93 | 57.01 |  |
| --- | --- | --- | --- | --- | --- |

| Peak load during pulses | 148.41 | 0.90 | 133.73 | 64.36 |  |
| --- | --- | --- | --- | --- | --- |

The following is a description of various details related to the requirements listed in Table AC-3.1-1:

a. Any combination of pulsed load and repetition period with ∫i2(t)dt less than or equal to that described by the nominal loading scenario shall be possible, as long as the repetition period is not less the minimum NSTX repetition period and as long as the peak active and

reactive power demands do not exceed the nominal maximum values given in Table AC-3.1-1.

b. Voltage variations and distortion at PPPL's 138 kV bus, under regular operating conditions shall conform to IEEE 519, "IEEE Guide for Harmonic Control and Reactive Compensation of Static Power Converters".

c. Voltage variations at PPPL's 138 kV bus, under unusual and fault conditions (such as load shed or short circuit) shall be limited to less than +/-10%.

d. Harmonic content of the line current at PPPL's 138 kV bus shall not exceed that of a 12 pulse rectifier, i.e.:

harmonic:  				11th    13th    23rd      25th

rms % of fundamental:      		9         7.5       4.5          4

e. Operation at full rating shall not be restricted to any particular time of day.

f. Experimental power loads from other machines at PPPL shall be assumed inactive or not coincident with NSTX. However, the auxiliary systems loads from other experiments at the laboratory shall be considered coincidental, including those due to D-site.

g. Any restrictions concerning the simultaneous operation of NSTX and the operation of the D-site MG sets shall be explicitly identified.

3.2 Experimental Power Component of Load

Table AC-3.2-1 itemizes and sums the experimental power loads.

Table AC-3.2-1: Experimental Power Loads

|  | MW | Eff | MVA | pf | MW | MVAR | Source | Ref |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| TF (between pulse) |  |  | 0.0 | 0.80 | 0.0 | 0.0 | Q1,Q2 | 86 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| TF (during pulse) |  |  | 0.0 | 0.00 | 0.0 | 0.0 | Q1,Q2 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| PF1 |  |  | 67.6 | 0.96 | 64.8 | 19.3 | S2 | PF-3.2.4-2 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| PF2-8 |  |  | 11.5 | 0.64 | 7.3 | 8.9 | Q1 | PF-3.2.4-2 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| HHFW (per source) | 2.00 | 0.50 | 4.4 | 0.90 | 4.0 | 1.9 | Q6 | 29 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| ECH (per source) | 0.20 | 0.25 | 0.9 | 0.90 | 0.8 | 0.4 | Q6 | 33 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| NBI | 2.00 | 0.45 | 4.9 | 0.90 | 4.4 | 2.2 | Q6 | 37 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| CHI (during pulse) |  |  | 6.7 | 0.75 | 5.0 | 4.4 | Q1 | CHI-3.1-1 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| Baseline | # | MW | MVA | pf | MW | MVAR |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| TF |  |  | 0.0 | 0.00 | 0.0 | 0.0 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| PF1 |  |  | 67.6 | 0.96 | 64.8 | 19.3 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| PF2-8 |  |  | 11.5 | 0.64 | 7.3 | 8.9 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| HHFW | 3.00 | 0.60 | 13.3 | 0.90 | 12.0 | 5.8 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| ECH | 1.00 | 2.00 | 0.9 | 0.90 | 0.8 | 0.4 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| CHI |  |  | 6.7 | 0.75 | 5.0 | 4.4 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| Q1 |  |  | 18.1 | 0.68 | 12.3 | 13.3 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| Q6 |  |  | 14.2 | 0.90 | 12.8 | 6.2 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| S2 |  |  | 67.6 | 0.96 | 64.8 | 19.3 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| Tot Input (between pulse) |  |  | 0.0 | 0.00 | 0.0 | 0.0 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| Tot Input (during pulse) |  |  | 107.7 | 0.92 | 98.9 | 42.7 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| NBI Upgrade | # | MW | MVA | pf | MW | MVAR |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| TF |  |  | 0.0 | 0.0 | 0.0 | 0.0 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| PF1 |  |  | 67.6 | 1.0 | 64.8 | 19.3 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| PF2-8 |  |  | 11.5 | 0.6 | 7.3 | 8.9 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| HHFW | 3.00 | 0.60 | 13.3 | 0.9 | 12.0 | 5.8 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| ECH | 1.00 | 2.00 | 0.9 | 0.9 | 0.8 | 0.4 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| CHI |  |  | 6.7 | 0.8 | 5.0 | 4.4 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| NBI | 4.00 | 8.00 | 19.8 | 0.90 | 17.8 | 8.6 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| Q1 |  |  | 18.1 | 0.68 | 12.3 | 13.3 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| Q6 |  |  | 40.4 | 0.88 | 35.6 | 19.2 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| S2 |  |  | 67.6 | 0.96 | 64.8 | 19.3 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| Tot Input (between pulse) |  |  | 0.0 | 0.00 | 0.0 | 0.0 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| Tot Input (during pulse) |  |  | 136.4 | 0.91 | 123.9 | 57.0 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

The following is a description of various details related to the requirements listed in Table AC-3.2-1:

a. Input power levels given in Table AC-3.2-1 are 110% of required outputs, to account for transformer and line losses.

b. Long Pulse Upgrade loads shall be assumed identical to the NBI Upgrade except that long pulse operation is required.

c. The TF system is assumed powered entirely from the C-site generators during a pulse; the motors are off, and no TF power is derived from the grid.

d. Any combination of pulsed load and repetition period with ∫i2(t)dt less than or equal to that described by the nominal loading scenario shall be possible, as long as the repetition period is not less than the minimum NSTX repetition period and as long as the peak active and reactive power demands do not exceed the nominal maximum values given in Table AC-3.2.

3.3 Auxiliary Systems Component of Load

Input and output requirements are summarized in Table AC-3.3-1.

Table AC-3.3-1: Auxiliary Power Loads

| Description | MVA | p.f. | MW | MVAR | Ref |
| --- | --- | --- | --- | --- | --- |

| WBS 2 Heating Systems | 0.500 | 0.800 | 0.400 | 0.300 | 41 |
| --- | --- | --- | --- | --- | --- |

| WBS 2 Heating Systems (NBI Upgrade) | 0.500 | 0.800 | 0.400 | 0.300 | 42 |
| --- | --- | --- | --- | --- | --- |

| WBS 3 Auxiliary Systems | 1.000 | 0.800 | 0.800 | 0.600 | 43 |
| --- | --- | --- | --- | --- | --- |

| WBS 4 Plasma Diagnostics | 0.500 | 0.800 | 0.400 | 0.300 | 44 |
| --- | --- | --- | --- | --- | --- |

| WBS 5 Power Systems | 0.500 | 0.800 | 0.400 | 0.300 | 45 |
| --- | --- | --- | --- | --- | --- |

| WBS 6 Central I&C | 0.250 | 0.800 | 0.200 | 0.150 | 46 |
| --- | --- | --- | --- | --- | --- |

| WBS 8 Facilities | 0.750 | 0.800 | 0.600 | 0.450 | 47 |
| --- | --- | --- | --- | --- | --- |

| Total NSTX Aux Sys | 3.500 | 0.800 | 2.800 | 2.100 |  |
| --- | --- | --- | --- | --- | --- |

| Total NSTX Aux Sys (NBI Upgrade) | 3.500 | 0.800 | 2.800 | 2.100 |  |
| --- | --- | --- | --- | --- | --- |

WBS 52 -  Toroidal Field (TF) Power Conversion Requirements

1.0 Functions

a. The TF Power Conversion System shall be designed to provide a constant current in the TF magnets during an NSTX discharge based on a reference current input signal provided in real time.

2.0 Configuration Requirements & Essential Features

a. The TF Power Conversion System shall include all equipment necessary to power the TF coils. This shall include all equipment from the AC input power interface through to the DC bus connections to the magnets, consisting of the C-site MG sets, DC bus, disconnect switches and bus links, and all associated monitoring, control, and protection equipment.

b. Bus links or other means shall be provided in order that the current in the TF magnets can be driven in either direction. However the toroidal field direction shall always be opposite to the plasma current direction. The polarity reversal procedure shall require 4 hours or less [R9]

c. No-load disconnect switches shall be provided to isolate the TF Power Conversion System from the connections to the TF magnets. In addition, no-load grounding switches shall be provided to ground the terminals of the connections to the TF magnets. These switches shall be interlocked with test cell access control [R9]..

d. The TF power system equipment shall be equipped with a local control system which shall include provisions for closed loop current control using proportional (P) and integral (I) feedback to effect tracking of reference signals.

e. The TF Power Conversion System shall include protection to avoid the delivery of current which would overheat the TF magnets, assuming that their coolant conditions are nominal [R9]..

f. Redundant measurements of TF current shall be provided [R9].

g. Voltage measurements shall be made from both bus terminals to ground. Frequency response shall be DC to 1MHz minimum.

h.  The TF power  system  shall be grounded via high resistance connections at the (+) and (-) coil terminals.  A ground fault protection system shall be used in conjunction with the grounding scheme to detect grounds within the TF circuit.

i. The TF power system equipment and bus system external to the test cell shall be totally enclosed so that access can be maintained around the operating equipment without danger to the personnel.

3.0 Performance & Operational Requirements

3.1 Baseline Operation

Basic requirements are summarized in Table TF-1.3-1.

Table TF-1.3.-1: TF Requirements

| Parameter | Value | Units | Ref |
| --- | --- | --- | --- |

| Major Radius R | 0.80 | m | 48 |
| --- | --- | --- | --- |

| TF Coil # Turns | 72 | turns | 49 |
| --- | --- | --- | --- |

| TF Coil Inductance | 0.017 | henries | 50 |
| --- | --- | --- | --- |

| Max Allowable Equivalent Square Wave | 6.0 | sec | 51 |
| --- | --- | --- | --- |

| TF Resistance vs. I2T Function C0 | 2.0874E-02 | Ω | 52 |
| --- | --- | --- | --- |

| TF Resistance vs. I2T Function C1 | 3.3314E-12 | Ω/A^2-s | 53 |
| --- | --- | --- | --- |

| TF Resistance vs. I2T Function C2 | 3.6422E-22 | Ω/(A^2-s)^2 | 54 |
| --- | --- | --- | --- |

| TF B - Baseline Pulse | 0.3200 | Tesla | 55 |
| --- | --- | --- | --- |

| TF Flat Top Duration - Baseline Pulse | 0.50 | sec | 56 |
| --- | --- | --- | --- |

| TF Repetition Period - Baseline Pulse | 600.00 | sec | 57 |
| --- | --- | --- | --- |

| TF B - High Field Pulse | 0.6400 | Tesla | 58 |
| --- | --- | --- | --- |

| TF Flat Top Duration - High Field Pulse | 0.60 | sec | 59 |
| --- | --- | --- | --- |

| TF Repetition Period - High Field Pulse | 600.00 | sec | 60 |
| --- | --- | --- | --- |

| TF B - Long Pulse | 0.3200 | Tesla | 61 |
| --- | --- | --- | --- |

| TF Flat Top Duration - Long Pulse | 60.00 | sec | 62 |
| --- | --- | --- | --- |

| TF Repetition Period - Long Pulse | 72000.00 | sec | 63 |
| --- | --- | --- | --- |

| TF Current Measurement Accuracy | 1 | % | 64 |
| --- | --- | --- | --- |

| TF Current Control Accuracy | 1 | % | 65 |
| --- | --- | --- | --- |

The following are points of elaboration with regard to Table TF-1.3-1:

a. The Equivalent Square Wave (ESW) is the time duration of a constant current (equal to the current required to produce the required magnetic field) for which the ∫i2(t)dt produces the maximum allowable coil temperature rise under adiabatic conditions. The current waveform in actual operation shall have an ∫i2(t)dt which is less than or equal to that given by the ESW.

b. The TF Resistance vs. ∫i2(t)dt is characterized by a function of the form:

R = C0 + C1 * X + C2 * X2

where:

R 		= total TF coil circuit resistance in ohms

X 		= ∫i2(t)dt in amp2-seconds

C0, C1, C2	= coefficients given in Table TF-1.3-1

c. Current measurement accuracy specification is defined as the absolute value of the difference between the measured value and the actual value as a percentage of the full scale value.

d. The current control accuracy specification corresponds to steady state conditions and is defined as the difference between the measured average current and the reference current as a percentage of the full scale current, excluding measurement errors.

The derived TF ampacity requirements are summarized in Table TF-1.3-2.

Table TF-1.3.-2 TF Ampacity Requirements

| Parameter | Value | Units | Ref |
| --- | --- | --- | --- |

| Baseline Pulse Current | 17777.8 | Amp |  |
| --- | --- | --- | --- |

| Baseline Pulse ESW | 6.0 |  | 51 |
| --- | --- | --- | --- |

| Baseline Pulse ∫i^2dt | 1.90E+09 | amp^2-sec |  |
| --- | --- | --- | --- |

| Baseline Pulse Repetition Period | 600.0 | sec | 57 |
| --- | --- | --- | --- |

| Baseline Pulse Irms | 1777.8 | amps |  |
| --- | --- | --- | --- |

| High Field Pulse Current | 35555.6 | Amp |  |
| --- | --- | --- | --- |

| High Field Pulse ESW | 1.5 |  |  |
| --- | --- | --- | --- |

| High Field Pulse ∫i^2dt | 1.90E+09 | amp^2-sec |  |
| --- | --- | --- | --- |

| High Field Pulse Repetition Period | 600.0 | sec |  |
| --- | --- | --- | --- |

| High Field Pulse Irms | 1777.8 | amps |  |
| --- | --- | --- | --- |

| Baseline Minimum Coil Resistance | 2.0874E-02 | Ω |  |
| --- | --- | --- | --- |

| Baseline Maximum Coil Resistance | 2.8501E-02 | Ω |  |
| --- | --- | --- | --- |

| Energy per Baseline Pulse | 4.53E+07 | Joule |  |
| --- | --- | --- | --- |

| Long Pulse Current | 17777.8 | amps |  |
| --- | --- | --- | --- |

| Long Pulse ESW | 60.0 | sec | 62 |
| --- | --- | --- | --- |

| Long Pulse ∫i^2dt | 1.90E+10 | amp^2-sec |  |
| --- | --- | --- | --- |

| Long Pulse Repetition Period | 72000.0 | sec |  |
| --- | --- | --- | --- |

| Long Pulse Irms | 513.2 | amps |  |
| --- | --- | --- | --- |

The following are points of elaboration with regard to Table TF-1.3-2:

a. The TF power supply system shall be capable of driving the coil current from zero to full current, regulating the current at the specified flat top value for the specified flat top period, and then driving the current to zero. The ∫i2(t)dt of the resultant waveform shall be within the specified limit.

b. In case of a fault the TF power supply shall shut down in such a way that the maximum ∫i2(t)dt of the pre-fault and post-fault current waveform does not exceed the maximum value given Table TF-1.3-2.

3.1 Upgrades

a. None of the upgrade requirements are imposed on the baseline TF Power Conversion System [R3].

WBS 53 -  Poloidal Field/Ohmic Heating (PF/OH) Requirements

1.0 Functions

a. The PF/OH Power Conversion System shall provide a variable current in the PF and OH magnet circuits  during an NSTX discharge based on a reference current input signal provided in real time [R10].

2.0 Configuration Requirements & Essential Features

a. The PF/OH Power Conversion System shall include all of the equipment necessary to power the PF coils.  This includes all equipment from the primary terminals of the converter transformers through to the DC bus connections to the magnets, consisting of phase controlled thyristor converters, DC breaker and resistor insertion equipment, DC bus, disconnect switches and bus links, and all associated monitoring, and protection equipment.

b. The PF coils shall be connected in series groups in galvanically separate circuits with independent current control as indicated in Table PF-2.0-1 [R11].

Table PF-2.0-1: Galvanically Separate PF Circuits

| PF Circuit | Coil Grouping |
| --- | --- |

| 1 | OH |
| --- | --- |

| 2 | PF1a, upper & lower |
| --- | --- |

| 3 | PF1b, upper & lower |
| --- | --- |

| 4 | PF2a, upper & lower |
| --- | --- |

| 5 | PF2b upper |
| --- | --- |

| 6 | PF2b lower |
| --- | --- |

| 7 | PF3a, PF3b, upper & lower |
| --- | --- |

| 8 | PF4a, PF4b, PF4c, upper & lower |
| --- | --- |

c. All series coil connections indicted in Table PF-2-1 shall result in current flow which is equal in magnitude, and in the same φ direction, in the upper and lower coils [R11].

d. All PF circuits except for OH shall be unipolar during a pulse [R10].

e. Bus links shall be provided to permit the connection of the available C-site power supplies to the PF2 through PF8 circuits in a variety of configurations.

f. Bus links or other means shall be provided in order that the current in the PF magnets can be driven in either direction. The polarity reversal procedure shall require 4 hours or less [R10].

g. No-load disconnect switches shall be provided to isolate the PF Power System from the connections to the PF magnets. In addition, no-load grounding switches shall be provided to ground the terminals of the connections to the PF magnets. These switches shall be interlocked with test cell access control [R10].

h. Redundant measurements of each PF current shall be provided [R10].

i. The PF Power Conversion System shall include protection to avoid the delivery of current which would overheat the PF magnets, assuming that their coolant conditions are nominal [R10].

3.0 Performance & Operational Requirements

3.1 Description of PF/OH Coils

The PF coils are described by their basic geometry as summarized in Table PF-3.1-1 [R66], and their properties as summarized in Table PF-3.1-2.

Table PF-3.1-1: PF/OH Coil Geometry

| Coil | R (center) | ∆R | Z (center) | ∆Z | Turns | Fill | Cond | Ref |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

|  | (cm) | (cm) | (cm) | (cm) |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| OHa | 12.80 | 4.60 | 55.09 | 110.18 | 294 | 0.6701 | Cu | 66 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| OHb | 12.80 | 4.60 | 161.62 | 102.64 | 92 | 0.7475 | Cu | 66 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| OHc | 17.60 | 4.20 | 155.82 | 93.52 | 88 | 0.7348 | Cu | 66 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| PF1a | 27.57 | 3.40 | 155.82 | 78.88 | 92 | 0.6311 | Cu | 66 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| PF1b | 31.17 | 3.40 | 156.38 | 65.44 | 76 | 0.6284 | Cu | 66 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| PF2a | 79.92 | 16.27 | 193.35 | 6.80 | 13 | 0.6838 | Cu | 66 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| PF2b | 79.92 | 16.27 | 185.26 | 6.80 | 13 | 0.6838 | Cu | 66 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| PF3a | 149.45 | 18.64 | 163.35 | 6.80 | 15 | 0.6886 | Cu | 66 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| PF3b | 149.45 | 18.64 | 155.26 | 6.80 | 15 | 0.6886 | Cu | 66 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| PF4a | 178.27 | 6.78 | 72.75 | 6.80 | 5 | 0.6310 | Cu | 66 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| PF4b | 179.46 | 9.15 | 64.66 | 6.80 | 7 | 0.6544 | Cu | 66 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| PF4c | 180.65 | 11.53 | 56.57 | 6.80 | 9 | 0.6682 | Cu | 66 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

Table PF-3.1-2: PF Conductor Properties

| Parameter | Value | Units | Ref |
| --- | --- | --- | --- |

| Resistivity (20C) | 1.724E-06 | Ω-cm | 67 |
| --- | --- | --- | --- |

| Density | 8.9400 | gm/cc | 68 |
| --- | --- | --- | --- |

| Specific Heat | 0.3860 | J/gm-degC | 69 |
| --- | --- | --- | --- |

| Res Temp Coeff | 0.0041 | 1/degC | 70 |
| --- | --- | --- | --- |

| Initial Temp | 20.0 | degC | 71 |
| --- | --- | --- | --- |

Based on the coil grouping given in Table PF-2.0-1, the coil geometry given in Table PF-3.1-1, and the PF conductor properties given in Table PF-3.1-2, the PF circuit 20 C resistances are given in Tables PF-3.1-3 [R75], and the mutual inductance matrix is given in Table PF-3.1-4 [R75].

Table PF-3.1-2: PF Circuit Resistances

| Circuit | Resistance |
| --- | --- |

|  | Ω @ 20C |
| --- | --- |

| PF1 | 8.745E-02 |
| --- | --- |

| PF2 | 2.987E-02 |
| --- | --- |

| PF3 | 2.790E-02 |
| --- | --- |

| PF4 | 3.869E-03 |
| --- | --- |

| PF5 | 1.935E-03 |
| --- | --- |

| PF6 | 1.935E-03 |
| --- | --- |

| PF7 | 1.670E-02 |
| --- | --- |

| PF8 | 1.405E-02 |
| --- | --- |

Table PF-3.1-3: PF Mutual Inductance Matrix (mH)

|  | PF1 | PF2 | PF3 | PF4 | PF5 | PF6 | PF7 | PF8 | Plasma |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| PF1 | 12.9380 | 2.9196 | 2.3939 | 0.2568 | 0.1392 | 0.1392 | 0.6631 | 0.5293 | 0.0159 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| PF2 | 2.9196 | 4.5992 | 4.0463 | 0.3361 | 0.1832 | 0.1832 | 0.6580 | 0.3098 | 0.0035 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| PF3 | 2.3939 | 4.0463 | 4.4516 | 0.3602 | 0.1986 | 0.1986 | 0.7089 | 0.3252 | 0.0035 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| PF4 | 0.2568 | 0.3361 | 0.3602 | 0.9629 | 0.3744 | 0.3744 | 0.7575 | 0.2639 | 0.0019 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| PF5 | 0.1392 | 0.1832 | 0.1986 | 0.3744 | 0.4793 | 0.0023 | 0.3619 | 0.1411 | 0.0011 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| PF6 | 0.1392 | 0.1832 | 0.1986 | 0.3744 | 0.0023 | 0.4793 | 0.4720 | 0.1411 | 0.0011 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| PF7 | 0.6631 | 0.6580 | 0.7089 | 0.7575 | 0.3619 | 0.4720 | 8.1498 | 2.1419 | 0.0133 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| PF8 | 0.5293 | 0.3098 | 0.3252 | 0.2639 | 0.1411 | 0.1411 | 2.1419 | 7.7776 | 0.0255 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| Plasma | 0.0159 | 0.0035 | 0.0035 | 0.0019 | 0.0011 | 0.0011 | 0.0133 | 0.0255 | 0.0001 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

3.2 Baseline Operation

3.2.1 PF Equilibria Requirements

Table PF-3.2.1-1 gives the required kA-turns for PF circuits 2 through 8 for the interval between SOF and EOF, for the various scenarios which are each characterized by a particular plasma internal inductance (li), aspect ratio (A), elongation (κ), and triangularity (δ) [R76].

Table PF-3.2.1-1: PF Equilibria Current Distributions

|  | li | A | κ | δ | I2 | I3 | I4 | I5 | I6 | I7 | I8 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| I-a | 0.6 | 1.25 | 2.01 | 0.46 | 0.0 | -75.0 | 0.0 | 0.0 | 0.0 | 70.0 | 231.0 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| I-b | 0.2 | 1.25 | 2.03 | 0.52 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 170.0 | 150.0 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| II-a | 0.6 | 1.25 | 2.01 | 0.46 | 0.0 | -75.0 | 0.0 | 0.0 | 0.0 | 70.0 | 231.0 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| II-b | 0.2 | 1.25 | 2.03 | 0.52 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 170.0 | 150.0 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| II-c | 0.6 | 1.40 | 0.00 | 0.00 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| II-d | 0.2 | 1.40 | 0.00 | 0.00 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| III-a | 0.6 | 1.25 | 2.20 | 0.49 | 0.0 | -50.0 | -50.0 | -50.0 | -50.0 | 139.0 | 216.0 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| III-b | 0.2 | 1.25 | 2.20 | 0.53 | 0.0 | 0.0 | -50.0 | -50.0 | -50.0 | 369.0 | 102.0 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| III-c | 0.6 | 1.40 | 2.39 | 0.39 | 0.0 | -431.0 | 0.0 | 0.0 | 0.0 | 0.0 | 308.0 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| III-d | 0.2 | 1.40 | 3.00 | 0.49 | 0.0 | -40.0 | -105.5 | -105.5 | -105.5 | 0.0 | 0.0 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| IV-a | 0.6 | 1.25 | 0.00 | 0.00 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| IV-b | 0.2 | 1.25 | 0.00 | 0.00 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| IV-c | 0.6 | 1.40 | 0.00 | 0.00 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| IV-d | 0.2 | 1.40 | 0.00 | 0.00 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

The above currents correspond to Ip = 1.0 MA in the negative  φ direction.

3.2.2 Current Requirements

A typical PF1 (OH) current waveform is depicted in figure PF-3.2.2-1. The required peak current is given in Table PF-3.2.2-1.

Figure PF-3.2-1: OH Current Waveform

The plasma ramp up and ramp down times which determine the PF1 scenario shall be as limited by the available PF1 and PF2-8 power supplies. The flat top time shall be as required for the inductive scenario, Scenario I. The precharge time shall be sufficiently short so as to limit the adiabatic temperature rise of the OH coil to 80 deg C.

The following assumptions were made to determine the ampacity requirements of the other PF circuits (PF2-PF8):

- it is assumed that the PF power supplies may be energized for the full TF flat top duration (SOFTF to EOFTF) at their full rated current;

- based on adiabatic coil heating considerations and the above assumption the highest feasible power supply current rating is assumed in each circuit;

- it is assumed that the above current could be repeated with the minimum repetition interval.

The PF ampacity requirements are summarized in Table PF-3.2.2-1 [R75].

Table PF-3.2.2-1: PF Ampacity Requirements

| Circuit | Max Curr | Max ESW | Max ∫i^2(t)dt | Max Irms |
| --- | --- | --- | --- | --- |

|  | kA | sec | A^2-sec | kA |
| --- | --- | --- | --- | --- |

| PF1 | 20.0 | 0.45 | 1.800E+08 | 0.548 |
| --- | --- | --- | --- | --- |

| PF2 | 5.0 | 5.00 | 1.250E+08 | 0.456 |
| --- | --- | --- | --- | --- |

| PF3 | 5.0 | 5.00 | 1.250E+08 | 0.456 |
| --- | --- | --- | --- | --- |

| PF4 | 20.0 | 5.00 | 2.000E+09 | 1.826 |
| --- | --- | --- | --- | --- |

| PF5 | 20.0 | 5.00 | 2.000E+09 | 1.826 |
| --- | --- | --- | --- | --- |

| PF6 | 20.0 | 5.0 | 2.000E+09 | 1.826 |
| --- | --- | --- | --- | --- |

| PF7 | 20.0 | 5.0 | 2.000E+09 | 1.826 |
| --- | --- | --- | --- | --- |

| PF8 | 20.0 | 5.0 | 2.000E+09 | 1.826 |
| --- | --- | --- | --- | --- |

3.2.3 Voltage Requirements

The coil voltage requirements are determined by the OH precharge and plasma ramp up and ramp down rates, as well as the resistive voltage drops. The precharge and ramp rates shall be constrained by the voltage capability of the C-site power supplies. The ramp rates and plasma current flat top durations, for the inductive and non-inductive scenarios, which are assumed for the purposes of requirements definition are given in Table 3.2.3-1[R77].

Table PF-3.2.3-1: PF Ramp and Flat Top Times (sec)

|  | Ind | Non-Ind |
| --- | --- | --- |

| Tcharge | 0.25 | na |
| --- | --- | --- |

| Trise | 0.30 | 0.45 |
| --- | --- | --- |

| Tfall | 0.30 | 0.45 |
| --- | --- | --- |

| Tflat | 0.50 | 4.10 |
| --- | --- | --- |

Based on the coil mutual matrix, the various plasma equilibrium current distributions, the assumed ramp rates, and the coil resistances (assumed constant at their final value after application of the scenario ∫i2(t)dt), an estimate of the maximum and minimum required coil terminal voltages is given in Table 3.2.3-2 [R77], along with the maximum scenario current and ∫i2(t)dt), and the coil losses and final temperatures.

Table PF-3.2.3-2: PF Scenario Voltage, Current, ∫i2(t)dt, Loss, and Temperature

|  | PF1 | PF2 | PF3 | PF4 | PF5 | PF6 | PF7 | PF8 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| Vmax | 3.239 | 0.000 | 0.226 | 0.068 | 0.034 | 0.034 | 0.416 | 0.406 | kV |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| Vmin | -2.722 | 0.000 | -0.151 | -0.036 | -0.018 | -0.018 | -0.205 | -0.251 | kV |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| Imax | 20.000 | 0.000 | 5.671 | 8.115 | 8.115 | 8.115 | 12.300 | 14.667 | kA |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| ∫i^2(t)dt | 180.0 | 0.0 | 141.5 | 289.8 | 289.8 | 289.8 | 665.7 | 946.5 | kA^2-sec |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| Wloss | 17.7 | 0.0 | 4.1 | 1.1 | 0.6 | 0.6 | 11.3 | 13.7 | MJ |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| Tmax | 96.9 | 20.0 | 41.7 | 24.2 | 24.2 | 24.2 | 29.9 | 34.2 | deg C |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

3.2.4 Power Requirements

In order to estimate the active, reactive, and apparent power requirements, a power supply topology must be assumed. The power supply assignments assumed for the purposes of estimating the power requirements are given in Table 3.2.4-1 [R77].

Table PF-3.2.4-1: PF Power Supply Assignments

| PS# | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| Vmax | 4000.0 | 300.0 | 300.0 | 300.0 | 300.0 | 200.0 | 500.0 | 500.0 | V |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| Imax | 24.0 | 5.0 | 5.0 | 5.0 | 5.0 | 10.0 | 20.0 | 5.0 | kA |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| Ckt Usage |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| I-a | PF1 | PF3 | PF7 |  |  |  | PF8 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| I-b | PF1 |  | PF7 | PF7 |  |  | PF8 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| II-a |  | PF3 | PF7 |  |  |  | PF8 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| II-b |  |  | PF7 |  |  |  | PF8 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| II-c |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| II-d |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| III-a |  | PF3 | PF7 | PF4,5,6 |  |  | PF8 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| III-b |  |  |  | PF8 |  | PF4,5,6 | PF7 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| III-c |  | PF3 |  |  |  |  | PF8 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| III-d |  | PF3 |  | PF8 |  | PF4,5,6 | PF7 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| IV-a |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| IV-b |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| IV-c |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| IV-d |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

The estimated maximum instantaneous (but not simultaneous) active and reactive power demands are given in Table PF-3.2.4-2 [R77].

Table PF-3.2.4-2: Instantaneous (non-simultaneous) Active and Reactive Power Maximums

|  | ∑PF | ∑PF1 | ∑PF2-8 |
| --- | --- | --- | --- |

| Max P | 64.783 | 64.783 | 7.304 |
| --- | --- | --- | --- |

| Max Q | 23.019 | 19.310 | 8.886 |
| --- | --- | --- | --- |

The PF1 (OH) circuit has the highest power demand of all of the PF circuits. In order to limit the reactive power demand, the above results assume the use of sequential control of the series connected rectifiers which comprise the PF1 power supply. For the purposes of estimating the total peak AC input power required (for WBS 51), the above active and reactive power demands will be assumed coincidental.

3.2.5 Other Requirements

PF/OH Current measurement and control accuracy requirements are given in Table PF-3.2.5-1.

Table PF-3.2.5-1: PF Measurement and Control Accuracy Requirements

| Parameter | Value | Units | Ref |
| --- | --- | --- | --- |

| Current Measurement Accuracy | 0.1 | % | 78 |
| --- | --- | --- | --- |

| Current Control Accuracy | 0.5 | % | 79 |
| --- | --- | --- | --- |

a. Current measurement accuracy specification is defined as the absolute value of the difference between the measured value and the actual value as a percentage of the full scale value.

b. The current control accuracy specification corresponds to steady state conditions and is defined as the difference between the measured average current and the reference current as a percentage of the full scale current, excluding measurement errors.

3.2 Upgrades

a. None of the upgrade requirements are imposed on the baseline TF Power Conversion System [R3].

WBS 54 -  CHI Power Conversion System Requirements

1.0 Functions

a. The function of the CHI power system (WBS 54) is to energize the CHI electrodes and impart a poloidal component of current flow in the plasma. The power supply consists of an energy storage capacitor bank with associated charge/discharge equipment along with an additional power supply to provide current after the capacitor bank discharge.

2.0 Configuration Requirements & Essential Features

a. CHI Power System shall be designed to provide a capacitor bank discharge followed by a power supply driven current [R13]. The power supply shall be a two-quadrant thyristor converter (+/-V, +I) controllable in either of two modes, namely:

- closed loop current control against a time varying reference current

- open loop voltage control against a time varying reference voltage

b. A fast acting crow-bar circuit shall be provided to divert the capacitor bank discharge from the NSTX machine on command [R13].

c. Bus links or other means shall be provided in order that the current in the CHI circuit can be driven in either direction. The polarity reversal procedure shall require 4 hours or less [R13].

d. No-load disconnect switches shall be provided to isolate the CHI Power System from the connections to the CHI magnets. In addition, no-load grounding switches shall be provided to ground the terminals of the connections to the CHI magnets. These switched shall be interlocked with test cell access control [R13].

e. Redundant measurements of CHI current shall be provided [R13].

3.0 Performance & Operational Requirements

3.1 Baseline Operation

Table CHI 3.1-1 CHI Power System Requirements

| Parameter | Value | Units | Ref |
| --- | --- | --- | --- |

| Capacitor Energy | 3.00E+06 | Joule | 80 |
| --- | --- | --- | --- |

| Capacitor Voltage | 1.50E+04 | Volt | 81 |
| --- | --- | --- | --- |

| Capacitor Capacitance | 2.67E-02 | Farad |  |
| --- | --- | --- | --- |

| PS Full Load Curr | 10000 | Amp | 82 |
| --- | --- | --- | --- |

| PS Full Load Voltage | 500 | Volt | 83 |
| --- | --- | --- | --- |

| PS Requlation | 25 | % |  |
| --- | --- | --- | --- |

| PS No Load Voltage | 666.7 | Volt |  |
| --- | --- | --- | --- |

| Pulse Duration | 5.0 | sec | 21 |
| --- | --- | --- | --- |

| Repetition Period | 300.0 | sec | 22 |
| --- | --- | --- | --- |

| RMS Current | 1291.0 | amp |  |
| --- | --- | --- | --- |

| PS Active Power | 5.0 | MW |  |
| --- | --- | --- | --- |

| PS Reactive Power | 4.4 | MVAR |  |
| --- | --- | --- | --- |

| PS Apparent Power | 6.7 | MVA |  |
| --- | --- | --- | --- |

| Curr Meas Accuracy | 0.1 | % | 84 |
| --- | --- | --- | --- |

| Curr Control Accuracy | 0.5 | % | 85 |
| --- | --- | --- | --- |

The following is a description of various details related to the requirements:

a. The CHI power system shall be capable of operation with any set of waveforms and duty cycles characterized by peak current and ∫i2(t)dt within the maximum allowable values.

b. Closed loop current control shall utilize both proportional (P) and integral (I) terms in the control law. The current control error specification corresponds to steady state conditions and is defined as the difference between the measured average current and the reference current as a percentage of the full scale current, excluding measurement errors.

c. Voltage measurements shall be made from both bus terminals to ground. Frequency response shall be DC to 1MHz minimum.

d. Redundant current measurements shall be provided. Current measurement error specification is defined as the difference between the measured value and the actual value as a percentage of the full scale value.

e. The CHI circuit  shall be grounded via high resistance connections at the (+) and (-) machine terminals.  A ground fault protection system shall be used in conjunction with the grounding scheme to detect grounds within the CHI circuit.

f. The CHI power conversion equipment and bus system shall be totally enclosed so that access can be maintained around the operating equipment without danger to the personnel.

g. Means for the automatic disconnection and grounding of the CHI circuits shall be provided for isolation between the CHI power conversion and the NSTX machine. Actuation and interlocking shall be commensurate with safety requirements such that access to the test cell can be gained without taking additional measures to ensure electrical safety.

3.2 Upgrades

a. None of the upgrade requirements are imposed on the baseline CHI Power Conversion System [R3].

| R | Description | Value | Units | Reference |
| --- | --- | --- | --- | --- |

| 1 | Location of NSTX | na | na | GRD sec 1.1.1 |
| --- | --- | --- | --- | --- |

| 2 | Req'ts for compatibility with PBX | na | na | GRD sec 1.6 |
| --- | --- | --- | --- | --- |

| 3 | Baseline and Upgrade Req'ts | na | na | GRD sec 1.1.2 |
| --- | --- | --- | --- | --- |

| 4 | NSTX Scenario Descriptions | na | na | GRD sec 2.1.2.1 |
| --- | --- | --- | --- | --- |

| 5 | NSTX Upgrade Requirements | na | na | GRD sec 2.1.3 |
| --- | --- | --- | --- | --- |

| 6 | NSTX Operating Lifetime Requirements | na | na | GRD sec 2.1.2.3 |
| --- | --- | --- | --- | --- |

| 7 | Req'ts for Non-Simultaneous Pulsing | na | na | GRD sec 1.6.1 |
| --- | --- | --- | --- | --- |

| 8 | PPPL AC Power System Equivalent Circuit | na | na | "Analysis of TPX Pulsing of Utility Grid", TPX Memo 41-940502-PPPL/CNeumeyer-01 |
| --- | --- | --- | --- | --- |

| 9 | TF Configuation & Feature Req'ts | na | na | GRD sec 1.6.2 |
| --- | --- | --- | --- | --- |

| 10 | PF/OH Configuation & Feature Req'ts | na | na | GRD sec 1.6.3 |
| --- | --- | --- | --- | --- |

| 11 | PF Circuit Definition | na | na | GRD sec 1.2.3.1 |
| --- | --- | --- | --- | --- |

| 12 | CHI Configuration & Feature Req'ts | na | na | GRD sec 1.6.4 |
| --- | --- | --- | --- | --- |

| 13 |  |  |  |  |
| --- | --- | --- | --- | --- |

| 14 |  |  |  |  |
| --- | --- | --- | --- | --- |

| 15 |  |  |  |  |
| --- | --- | --- | --- | --- |

| 16 |  |  |  |  |
| --- | --- | --- | --- | --- |

| 17 |  |  |  |  |
| --- | --- | --- | --- | --- |

| 18 |  |  |  |  |
| --- | --- | --- | --- | --- |

| 19 | Inductive Maximum Pulse Duration | 0.50 | sec |  |
| --- | --- | --- | --- | --- |

| 20 | Inductive minimum Repetition period | 600.00 | sec |  |
| --- | --- | --- | --- | --- |

| 21 | Non-Inductive Maximum Pulse Duration | 5.00 | sec |  |
| --- | --- | --- | --- | --- |

| 22 | Non-Inductive Minimum Repetition Period | 300.00 | sec |  |
| --- | --- | --- | --- | --- |

| 23 | Upgrade maximum Pulse duration | 60.00 | sec |  |
| --- | --- | --- | --- | --- |

| 24 | Upgrade minimum Repetition period | 72000.00 | sec | Assumed on basis of rms equal to baseline |
| --- | --- | --- | --- | --- |

| 25 | Operating lifetime | 25.00 | years |  |
| --- | --- | --- | --- | --- |

| 26 | Baseline number of pulses | 50000.00 | pulses |  |
| --- | --- | --- | --- | --- |

| 27 | PPPL A,B,C,D site House Power | 8.75 | MVA |  |
| --- | --- | --- | --- | --- |

| 28 | PPPL A,B,C,D site House Power Factor | 0.80 | p.u. |  |
| --- | --- | --- | --- | --- |

| 29 | HHFW Power per Source to Plasma | 2.00 | MW |  |
| --- | --- | --- | --- | --- |

| 30 | HHFW Efficiency | 0.50 | p.u. |  |
| --- | --- | --- | --- | --- |

| 31 | HHFW Power Factor | 0.90 | p.u. |  |
| --- | --- | --- | --- | --- |

| 32 | HHFW Number of Sources | 3.00 | sources |  |
| --- | --- | --- | --- | --- |

| 33 | ECH Power per Source to Plasma | 0.20 | MW |  |
| --- | --- | --- | --- | --- |

| 34 | ECH Efficiency | 0.25 | p.u. |  |
| --- | --- | --- | --- | --- |

| 35 | ECH Power Factor | 0.90 | p.u. |  |
| --- | --- | --- | --- | --- |

| 36 | ECH Number of Sources | 1.00 | sources |  |
| --- | --- | --- | --- | --- |

| 37 | NBI Power per Source to Plasma | 2.00 | MW |  |
| --- | --- | --- | --- | --- |

| 38 | NBI Efficiency | 0.45 | p.u. |  |
| --- | --- | --- | --- | --- |

| 39 | NBI Power Factor | 0.90 | p.u. |  |
| --- | --- | --- | --- | --- |

| 40 | NBI Number of Sources (Upgrade) | 4.00 | sources |  |
| --- | --- | --- | --- | --- |

| 41 | WBS 2 Heating Sys Aux AC Power | 0.50 | MVA |  |
| --- | --- | --- | --- | --- |

| 42 | WBS 2 Heating Sys Aux AC Power (Upgrade) | 0.50 | MVA |  |
| --- | --- | --- | --- | --- |

| 43 | WBS 3 Auxiliary Sys Aux AC Power | 1.00 | MVA |  |
| --- | --- | --- | --- | --- |

| 44 | WBS 4 Diagnostics Aux AC Power | 0.50 | MVA |  |
| --- | --- | --- | --- | --- |

| 45 | WBS 5 Power Systems Aux AC Power | 0.50 | MVA |  |
| --- | --- | --- | --- | --- |

| 46 | WBS 6 Central I&C Aux AC Power | 0.25 | MVA |  |
| --- | --- | --- | --- | --- |

| 47 | WBS 8 Facilities Aux AC Power | 0.75 | MVA |  |
| --- | --- | --- | --- | --- |

| 48 | Major Radius R | 0.80 | m |  |
| --- | --- | --- | --- | --- |

| 49 | TF Coil # Turns | 72 | turns |  |
| --- | --- | --- | --- | --- |

| 50 | TF Coil Inductance | 0.017 | henries |  |
| --- | --- | --- | --- | --- |

| 51 | Max Allowable Equivalent Square Wave | 6.0 | sec |  |
| --- | --- | --- | --- | --- |

| 52 | TF Resistance vs. I2T Function C0 | 2.0874E-02 | Ω | "TF Resistance vs. I2T",13-960418-AWB-01 |
| --- | --- | --- | --- | --- |

| 53 | TF Resistance vs. I2T Function C1 | 3.3314E-12 | Ω/A^2-s |  |
| --- | --- | --- | --- | --- |

| 54 | TF Resistance vs. I2T Function C2 | 3.6422E-22 | Ω/(A^2-s)^2 |  |
| --- | --- | --- | --- | --- |

| 55 | TF B - Baseline Pulse | 0.3200 | Tesla |  |
| --- | --- | --- | --- | --- |

| 56 | TF Flat Top Duration - Baseline Pulse | 0.50 | sec |  |
| --- | --- | --- | --- | --- |

| 57 | TF Repetition Period - Baseline Pulse | 600.00 | sec |  |
| --- | --- | --- | --- | --- |

| 58 | TF B - High Field Pulse | 0.6400 | Tesla | GRD sec 2.1.2.1.c |
| --- | --- | --- | --- | --- |

| 59 | TF Flat Top Duration - High Field Pulse | 0.60 | sec | GRD sec 2.1.2.1.c |
| --- | --- | --- | --- | --- |

| 60 | TF Repetition Period - High Field Pulse | 600.00 | sec |  |
| --- | --- | --- | --- | --- |

| 61 | TF B - Long Pulse | 0.3200 | Tesla |  |
| --- | --- | --- | --- | --- |

| 62 | TF Flat Top Duration - Long Pulse | 60.00 | sec |  |
| --- | --- | --- | --- | --- |

| 63 | TF Repetition Period - Long Pulse | 72000.00 | sec |  |
| --- | --- | --- | --- | --- |

| 64 | TF Current Measurement Accuracy | 1 | % |  |
| --- | --- | --- | --- | --- |

| 65 | TF Current Control Accuracy | 1 | % |  |
| --- | --- | --- | --- | --- |

| 66 | PF Geometry Description | na |  |  |
| --- | --- | --- | --- | --- |

| 67 | Copper 20C Resistivity | 1.7240E-06 | Ω-cm |  |
| --- | --- | --- | --- | --- |

| 68 | Copper Density | 8.94 | gm/cc |  |
| --- | --- | --- | --- | --- |

| 69 | Copper Specific Heat | 0.386 | J/gm-degC |  |
| --- | --- | --- | --- | --- |

| 70 | Copper Resistance Temperature Coeff | 0.0041 | 1/degC |  |
| --- | --- | --- | --- | --- |

| 71 | Inlet Water Temperature | 20 | C |  |
| --- | --- | --- | --- | --- |

| 72 | Copper G vs. T | 100 | C |  |
| --- | --- | --- | --- | --- |

| 73 | Copper T vs. G | na |  |  |
| --- | --- | --- | --- | --- |

| 74 | Copper H vs. T | na |  |  |
| --- | --- | --- | --- | --- |

| 75 | PF Coil Description | na |  |  |
| --- | --- | --- | --- | --- |

| 76 | Plasma Equilbria PF Current Distributions | na |  |  |
| --- | --- | --- | --- | --- |

| 77 | PF Scenario Analysis | na |  |  |
| --- | --- | --- | --- | --- |

| 78 | PF Current Measurement Accuracy | 0.5 | % |  |
| --- | --- | --- | --- | --- |

| 79 | PF Current Control Accuracy | 0.5 | % |  |
| --- | --- | --- | --- | --- |

| 80 | CHI Capacitor Energy | 3.00E+06 | Joule |  |
| --- | --- | --- | --- | --- |

| 81 | CHI Capacitor Voltage | 1.50E+04 | Volt |  |
| --- | --- | --- | --- | --- |

| 82 | CHI Power Supply Full Load Current | 10000 | Amp |  |
| --- | --- | --- | --- | --- |

| 83 | CHI Power Supply Full Load Voltage | 500 | Volt |  |
| --- | --- | --- | --- | --- |

| 84 | CHI Current Measurement Accuracy | 0.1 | % |  |
| --- | --- | --- | --- | --- |

| 85 | CHI Current Control Accuracy | 0.5 | % |  |
| --- | --- | --- | --- | --- |

| 86 | C-Site MG Idling Power per Shaft | 1 | MVA |  |
| --- | --- | --- | --- | --- |

| 86 |  |  |  |  |
| --- | --- | --- | --- | --- |

| 87 |  |  |  |  |
| --- | --- | --- | --- | --- |

| 88 |  |  |  |  |
| --- | --- | --- | --- | --- |

| 89 |  |  |  |  |
| --- | --- | --- | --- | --- |

| 90 |  |  |  |  |
| --- | --- | --- | --- | --- |