National Spherical Tokamak Experiment

NSTX

SYSTEM REQUIREMENTS DOCUMENT

CENTRAL INSTRUMENTATION & CONTROL (I&C)

NSTX-SRD-6X-012

Revision 0

July 15, 1996

________________________________

Dwight Bashore

WBS 6 Manager

________________________________

Charles Neumeyer

NSTX Project Engineering Manager

________________________________

Masa Ono

NSTX Project Manager

| Revision | Date | TRB | Description of Change |
| --- | --- | --- | --- |

Introduction	1

Central I&C System Requirements	2

1.0 Functions	2

2.0 Configuration Requirements & Essential Features	2

2.1 Location	2

2.2 Design Implementation Philosophy	3

3.0 Performance & Operational Requirements	3

3.1 Baseline Operation	3

3.2 Upgrades	4

Control System Requirements	5

1.0 Functions	5

1.1 Process Control System	5

1.2 Safety System	6

1.3 Control Room and Cable Tray System	6

1.4 Plasma Control System	7

2.0 Configuration Requirements & Essential Features	7

2.1 Process Control System	7

2.2 Safety System	7

2.3 Control Room and Cable Tray System	7

2.4 Plasma Control System	8

3.0 Performance & Operational Requirements	8

3.1 Baseline Operation	8

3.1.1 Process Control System	8

3.1.2 Safety System	9

3.1.3 Control Room and Cable Tray System	9

3.1.4 Plasma Control System	9

3.2 Upgrades	9

3.2.1 Process Control System	9

3.2.2 Safety System	9

3.2.3 Control Room and Cable Tray System	9

3.2.4 Plasma Control System	9

Data Acquisition System Requirements	10

1.0 Functions	10

1.1 Data Acquisition System	10

1.2 Synchronization System	11

2.0 Configuration Requirements & Essential Features	12

2.1 Data Acquisition System	12

2.2 Synchronization System	12

3.0 Performance & Operational Requirements	12

3.1 Baseline Operation	12

3.1.1 Data Acquisition System	12

3.1.2 Synchronization System	13

3.2 Upgrades	14

3.2.1 Data Acquisition System	14

3.2.2 Synchronization System	14

List of Tables

CI&C-2.1-1  Central I&C Room Name Cross-Reference	3

CS-1.1-1  NSTX Subsystems Supported By Central I&C's Process Control System	5

CS-2.2-1  Experimental Area Access Controlled Door Locations	7

CS-2.3-1  Cable Tray System Interconnected Locations	8

CS-3.1.1-1  Process Control System I/O Requirements	9

DA-1.1-1  List of Data Acquisition System Diagnostics	10

DA-3.1.1-1  Baseline Operation Requirements	13

DA-3.1.2-1  Definition of Events	13

DA-3.1.1-2  Upgrade Operation Requirements	14

List of FIGURES

APPENDIX

LIST OF REFERENCES

Introduction

This System Requirements Document (SRD) defines the design requirements of the Central Instrumentation and Control (I&C) System of the National Spherical Tokamak Experiment (NSTX).

The Central Instrumentation and Control System will provide remote control, monitoring, data acquisition and data management for the NSTX subsystems during machine operation.  The Central I&C System will provide researchers with access to the facility in support of the operation, physics planning, analysis and coordination of experimental objectives.

The Central I&C work package (WBS 6X) scope will include the design, installation, configuration and support for items such as the Process Control System, Safety System, Data Acquisition System, Synchronization System, the hardware portion of the Plasma Control System and the design, layout and installation of the Control Room and cable tray system.  The Central I&C work package will also develop standards for subsystem hardware and software elements and will provide consulting and coordination of each subsystem's local I&C effort.

A general section covers information which is relevant to the entire WBS element. Individual  subelements of the WBS Central I&C work scope are covered in separate sections, namely:

• WBS 61 Control System

• WBS 62 Data Acquisition System

Figures and Tables are numbered in format X-Y-Z where X=section (i.e. section abbreviation, e.g. CS for Control System), Y=paragraph number, and Z= sequence number within that paragraph.

References to the requirements identified herein are cited in the body of the document using serial numbers preceded by an "R" and are listed in the Appendix."

WBS 6X -  Central I&C System Requirements

1.0 Functions

a.  [R4>] The Central I&C system shall provide all supervisory control and monitoring of the NSTX facility, including:

• Plant Control and Monitoring (asynchronous routine control and monitoring)

• Plasma Control Processor and Input/Output Interface (digital processor and I/O 	hardware for  interface with plasma control measurements and actuators)

• Synchronization (synchronization of triggered actions from master clock events)

• Safety Interlock (master supervisory control of experiment)

• Access Control (control and monitoring of access to hazardous areas)

• Data Acquisition (periodic sampling, acquisition and display of regularly sampled data, and acquisition and display of data sampled and stored by remote devices)[<R4]

2.0 Configuration Requirements & Essential Features

2.1 Location

a.  [R1>] The NSTX machine shall be installed at the PPPL C-site C-cell (formerly occupied by the Princeton Large Torus (PLT)) [<R1].  The NSTX Central I&C System shall be installed at various locations at the PPPL C-site including the CS Building room C201 (formerly the PLT Control Room), the PPPL C-site COB Building room C221E (formerly the DAS Computer Room), the PPPL C-site CS Building C-cell room 102A (formerly occupied by the Princeton Large Torus (PLT)), the PPPL C-site M.G. Building room 101 Motor Generator Room, the C-site Systems Test Building (ESAT) and the Administration Building Computer Addition room A11D PPL Computer Center (PPLCC).

b.  Table CI&C-2.1-1 provides a naming cross-reference for room numbers associated with the NSTX Central I&C System.  Central I&C documentation will reference the assigned NSTX names.

TABLE .c.CI&C-2.1-1  Central I&C Room Name Cross-Reference;

2.2 Design Implementation Philosophy

a.  All new components of the Central I&C System shall employ only commercially-available off-the-shelf hardware and software.

b.  [R21>] For purposes of the design of NSTX, it shall be assumed that C-site and D-site equipment associated with TFTR operation is available for use on NSTX, except for equipment which is not readily transferable and does not lead to substantial cost savings.[<R21]

c. [R22>] For purposes of the design of NSTX, it shall be assumed that any equipment associated with PBX-M operation is not available for use on NSTX unless said equipment can be arranged so as to be available either for NSTX or PBX-M, with a time for transfer between one assignment and another of ≤ 4 hours [<R22].

3.0 Performance & Operational Requirements

3.1 Baseline Operation

a.  The Central I&C System shall accommodate the following baseline pulse repetition period and operating life requirements as defined in the General Requirements Document.  [R10>] The baseline NSTX machine shall be designed for a pulse repetition period of 300 seconds and a maximum of 100 pulses per 24 hour period.  The NSTX machine shall be designed to operate for a period of 10 years.  NSTX operation shall be assumed to consist of 100 pulses per day, 5 days per week, 3 weeks per month, 9 months per year, for 10 years (total of 135,000 pulses) [<R10].

b.  [R23>] All diagnostic signals shall be isolated via optical or magnetic means prior to exiting the test cell boundary. The isolation shall be rated to withstand a one minute AC hipot test at 20 kV AC rms [R23].

3.2 Upgrades

a.  The Central I&C System shall comply with the following guidance provided in the GRD regarding upgrades.  [R11>] The upgrades described herein are envisioned as possibilities which may or may not be undertaken, depending on experience gained with NSTX operation, and other factors. The baseline design of NSTX should facilitate the upgrades when possible without significant cost impact. As a minimum, the baseline design shall permit eventual upgrade and the upgrade path shall be identified as part of the baseline design process [<R11].

b. CHI Current Sustainment Power Supply Upgrade: The CHI current sustainment power supply would be required to provide a current of 20.0 kA at a power level of up to 15.0 MW, for the full duration SOD to EOD. The anticipated CHI Current Sustainment upgrade will require additional Central I&C System control, data acquisition, and data network capacity .

c.  Neutral Beam Injection (NBI) Upgrade:  [R12>] The NSTX design shall consider an upgrade which would place the four existing PBX-M sources on NSTX.  The baseline design for all NSTX components shall identify an upgrade path for the neutral beam upgrade [<R12].  [R2>] The anticipated Neutral Beam Injection (NBI) upgrade will require additional Central I&C System control, data acquisition, and data network capacity [<R2].

d. Long Pulse Upgrade:  [R13>] The NSTX design shall consider an upgrade which would remove the baseline TF and OH magnets, and place a new TF magnet in the center stack. The NSTX plasma pulse length shall be assumed to be 60 seconds for this upgrade.  The baseline design for all NSTX components shall identify an upgrade path for the long pulse operation [<R13].  [R3>] The anticipated long pulse upgrade will require additional Central I&C long pulse control and data acquisition capability [<R3].

WBS 61 -  Control System Requirements

1.0 Functions

1.1 Process Control System

a.  The NSTX Central I&C Process Control System shall provide remote control and/or monitoring of the NSTX subsystems listed in Table CS-1.1-1.

TABLE .c.CS-1.1-1  NSTX Subsystems Supported By Central I&C's Process Control System;

b.  [R5>] The Central I&C {process control system} shall provide reference signals to local I&C {process control} systems (provided by responsible WBS elements) for local feedback control, but is not required to close the loop for feedback control of plant processes [<R5].

c.  The process control system shall provide engineering displays in the NSTX Control Room to serve as the user interface to the engineering processes.  The engineering displays must provide current and historical trending, alarm logging, mimic displays, control capabilities, point monitoring and process control system status displays.

d.  The process control system shall support data transfer and inter-system communication via a dedicated Local Area Network.

1.2 Safety System

a.  All NSTX subsystems' equipment must have built-in self protection.  However, the NSTX Safety System shall provide system-wide coordination for personnel and hardware safety.

b.  The Safety System shall operate from an uninterruptable power source to ensure continuous operation.

c.  The Safety System shall provide monitoring, alarming, and logging of critical systems and invoke mitigating action to ensure personnel and hardware protection.

d.  The Safety System shall inhibit personnel access to the NSTX Test Cell if either the Electrical Safety Lockout Device (ESLD) or the Pneumatic Safety Lockout Device (PSLD) is in an unsafe position.

e.  The Safety System must control and monitor personnel entry, via the seven (7) existing doors, to the NSTX Test Cell to ensure personnel safety.  The Safety System shall ensure personnel safety before machine operation is permitted.

f.  The Safety System shall provide a continuously available user interface to the safety process.

g.  The Safety System's user interface shall present subsystem equipment permissive status, inter-system interlock status, ESLD status, PSLD status and access mode status.

h.  The transition of any subsystem equipment permissive status, inter-system interlock status, ESLD status, PSLD status and access mode status must be time tagged -- with time resolution capable of determining the sequence of events -- and reported to the safety displays.

i.  Various access modes will provide a foundation for operational interlocks that will regulate personnel access to the NSTX Test Cell.

1.3 Control Room and Cable Tray System

a.  The Control Room shall provide a centralized location for researchers to direct and monitor the experimental operation of the NSTX device.

b.  Provide access in the Control Room to the existing PPPL Ethernet network to support desktop computers, printers, and display terminals and provide the means for data transfer, inter-system communication and provide access to the ESnet and the Internet.

c.  Provide a cable tray system to economically and easily route power cables, signal cables and fiber optic cables throughout the NSTX facility.

d.  Provide furniture to support the engineering and experimental physics activities in the NSTX Control Room.

e.  Provide AC power distribution throughout the Control Room from the electrical distribution panel provided by WBS 5.

1.4 Plasma Control System

a.  Relocate the Digital Plasma Control System (DPCS), currently on TFTR, for use on NSTX.

b.  Configure the DPCS hardware to allow the system to be shared with PBX-M.

c.  Accommodate a remote I/O hardware capability.

2.0 Configuration Requirements & Essential Features

2.1 Process Control System

a.  All engineering subsystem monitoring of normal and abnormal conditions must be reported in the NSTX Control Room.

b.  The process control system must accommodate the sharing of subsystems that will be common to NSTX and PBX-M.

2.2 Safety System

a.  A fail safe electrical design must prevent machine operation should a single point of failure occur.

b.  The Safety System must operate from an uninterruptable power source.

c.  The locations of the seven (7) existing doors that provide access to the NSTX experimental area are listed in Table CS-2.2-1.

TABLE .c.CS-2.2-1  Experimental Area Access Controlled Door Locations;

2.3 Control Room and Cable Tray System

a.  The NSTX Control Room shall be installed in the location previously occupied by the PLT Control Room [R6].

b.  The Control Room layout shall facilitate interaction among experimental physicists and operations personnel to promote an interactive work environment.

c.  The Cable Tray System shall interconnect the locations identified in Table CS-2.3-1.

TABLE .c.CS-2.3-1  Cable Tray System Interconnected Locations;

2.4 Plasma Control System

a.  The SPARC 10 Host Computer and Console shall be located in an electrically safe area and where it is accessible to programmers and experimentalists.

b.  Remote I/O locations for the DPCS include the Test Cell and ESAT Building.

3.0 Performance & Operational Requirements

3.1 Baseline Operation

3.1.1 Process Control System

a.  Four (4) color engineering displays shall be provided in the NSTX Control Room to serve as the user interface to the engineering processes.  Each display shall measure a minimum of 19" diagonal and include a keyboard and a point-and-click device to accept user input.

b.  Trended process control monitor data must be maintained on-line for 30 days to support the display of historical trend data.  After 30 days, data shall be stored off-line for archival purposes.

c.  The NSTX process control system will need to support an estimated 1297 I/O points as outlined in Table CS-3.1.1-1.  Each I/O point requires a low scan rate (nominally 1 Hz) and is defined by one of the following general categories:

Analog Input ==> The system design must accommodate 4-20 mA, 0 to +5 VDC, 0 to +10 VDC, +/-2.5 VDC, +/-5 VDC, +/-10 VDC, thermocouple, RTD, and strain gauge interfaces.

Analog Output ==> The system design must accommodate 4-20 mA, 0 to +5 VDC, 0 to +10 VDC, +/-2.5 VDC, +/-5 VDC, and +/-10 VDC interfaces.

Digital Input ==> The system design must accommodate TTL, contact, +5 VDC, +12 VDC and +24 VDC interfaces.

Digital Output ==> The system design must accommodate TTL, Form "C" Relay, +5 VDC, +12 VDC and +24 VDC interfaces.

TABLE .c.CS-3.1.1-1  Process Control System I/O Requirements;

3.1.2 Safety System

3.1.3 Control Room and Cable Tray System

a.  The Control Room Network shall provide at least 10 MBit/Sec Bandwidth.

3.1.4 Plasma Control System

a.  The DCPS hardware configuration shall enable a 1 millisecond update frequency of the feedback control algorithm.

3.2 Upgrades

3.2.1 Process Control System

3.2.2 Safety System

3.2.3 Control Room and Cable Tray System

3.2.4 Plasma Control System

a.  Audio/Video for Remote Collaborations

WBS 62 -  Data Acquisition System Requirements

1.0 Functions

1.1 Data Acquisition System

a.  The Data Acquisition System shall gather data for the plasma diagnostics as well as the tokamak systems diagnostics, listed in Table DA-1.1-1, during machine operation.

TABLE .c.DA-1.1-1  List of Data Acquisition System Diagnostics;

b.  The Data Acquisition System shall provide physics displays in the NSTX Control Room to serve as the man/machine interface to support the physics research effort.

c.  The physics displays must support waveforms, which are graphical presentations of one or more data sets derived from time-dependent signals.  The waveform types shall be

described as fundamental waveforms (single input channel of data that may include elementary calculations to convert raw data into engineering units), composite waveforms (waveforms that require the results of one or more fundamental waveforms to calculate the resultant waveform), and model dependent waveforms (a waveform derived from a computer model which possibly uses fundamental or composite waveforms as inputs, i.e. TRANSP or SNAP).

d.  The Data Acquisition System must provide a data management structure to store, catalog and secure experimental results for subsequent retrieval and analysis.

e.  Data transport shall be provided via the Network System.

f.  [R7] The design of the I&C system shall facilitate access to archived NSTX data by parties outside of the NSTX control room (e.g. remote collaborators, physicists inside and outside of PPPL) in a read-only mode.

g. [R8>] The Central I&C system shall provide sixteen (16) electrically isolated, general purpose signal channels between the test cell and the control room. These signals shall be displayed in the control room in real-time [<R8].

h.  The Data Acquisition System Network shall provide a high-speed Local Area Network infrastructure for data transfer, inter-system communication, display of data, and user interface functions in support of the Central I&C Data Acquisition System.

i.  The Data Acquisition System must provide real-time (post-shot) analysis.

1.2 Synchronization System

a.  The Synchronization System shall generate and distribute synchronous events (preprogrammed) to the NSTX subsystems.  Synchronous events shall prescribe a predefined schedule of occurrences to be initiated at preselected times prior to, during, and after the operation of the experiment.

b.  The Synchronization System must generate and distribute a shot number that will be counted sequentially to uniquely identify each experiment.

c.  The Synchronization System must generate and distribute synchronized clock pulses to subsystems and the Central I&C System devices to initiate and execute time dependent processes by counting periodically generated clock pulses.

2.0 Configuration Requirements & Essential Features

2.1 Data Acquisition System

a.  The TFTR data handling resources shall be utilized to the maximum extent for NSTX data handling support.

b.  [R20>] The interface between the data highway and the diagnostic device control and data acquisition modules shall be a hybrid that can accommodate existing CAMAC equipment and hardware based on newer standards [<R20].

2.2 Synchronization System

b.  A man-machine interface to configure timing and event information shall be located in the NSTX Control Room.

3.0 Performance & Operational Requirements

3.1 Baseline Operation

3.1.1 Data Acquisition System

a.  Twelve (12) physics displays shall be provided in the NSTX Control Room to serve as the user interface to the experimental processes.

b.  [R20>] The tabulated data acquisition signals require sampling rates ranging from 100 Hz to 1 MHz and shall be used to meet NSTX diagnostics data acquisition requirements.  To establish requirements for Central I&C, each Data Acquisition signal is included in one of the following general categories:

Low Speed ==> Data Acquisition signals requiring sample rates >100 Hz and ≤2 KHz.

Moderate Speed ==> Data Acquisition signals  requiring sample rates >2 KHz and ≤100 KHz.

High Speed ==> Data Acquisition signals  requiring sample rates >100 KHz and ≤1 MHz.

The Average Sampling Time for each signal category (per NSTX pulse) is also included in the table below.

TABLE .c.DA-3.1.1-1  Baseline Operation Requirements;

c.  [R20>] The Day One and baseline diagnostics are expected to generate approximately 3.2 megabytes (MB) of data for each one-second pulse [<R20].

3.1.2 Synchronization System

a.  [R9] The Synchronization System must generate the sixteen (16) {synchronous (preprogrammed)} baseline events defined in Table DA-3.1.2-1.

Table .c.DA-3.1.2-1  Definition of Events;

| Name | Definition |
| --- | --- |

| SOP | Start of Pulse (start of power supply energization) |
| --- | --- |

| SOPTF | Start of Pulse TF (start of TF current) |
| --- | --- |

| SOPPF | Start of Pulse PF (start of PF current) |
| --- | --- |

| SOFTF | Start of Flat Top TF |
| --- | --- |

| SOI | Start of Initiation |
| --- | --- |

| EOI | End of Initiation |
| --- | --- |

| SOD | Start of Plasma Discharge |
| --- | --- |

| SOF | Start of Plasma Flat Top |
| --- | --- |

| SOX | Start of X-point |
| --- | --- |

| EOX | End of X-point |
| --- | --- |

| EOF | End of Plasma Flat Top |
| --- | --- |

| EOD | End of Plasma Discharge |
| --- | --- |

| EOFTF | End of Flat Top TF |
| --- | --- |

| EOPPF | End of Pulse PF (end of PF current) |
| --- | --- |

| EOPTF | End of Pulse TF (end of TF current) |
| --- | --- |

| EOP | End of Pulse (end of power supply energization) |
| --- | --- |

In addition to the 16 synchronous events listed above, the Synchronization System shall have a capacity for sixteen (16) additional events to accommodate a total baseline capacity of thirty-two (32) synchronous events.

b.  Simultaneity between data acquisition systems must be less than 10.0 usec.

3.2 Upgrades

3.2.1 Data Acquisition System

a.  [R20>]To establish requirements for Central I&C, each Data Acquisition signal is included in one of the following general categories:

Low Speed ==> Data Acquisition signals requiring sample rates >100 Hz and ≤2 KHz.

Moderate Speed ==> Data Acquisition signals  requiring sample rates >2 KHz and ≤100 KHz.

High Speed ==> Data Acquisition signals  requiring sample rates >100 KHz and ≤1 MHz.

The Average Sampling Time for each signal category (per NSTX pulse) is also included in the table below.

TABLE .c.DA-3.1.1-2  Upgrade Operation Requirements;

b.  [R20>] The upgrade diagnostics are expected to generate approximately 33.2 MB for each one-second pulse.  They should be increased by about a factor of five when the NSTX pulse duration is lengthened to five seconds [<R20].

3.2.2 Synchronization System

a.  Not applicable.