National Spherical Tokamak Experiment

NSTX

SYSTEM REQUIREMENTS DOCUMENT

CENTRAL INSTRUMENTATION & CONTROL (I&C)

NSTX-SRD-6X-012

Revision 0, Draft A

May 9, 1996

________________________________

Dwight Bashore

WBS 6 Manager

________________________________

Charles Neumeyer

NSTX Project Engineering Manager

________________________________

Masa Ono

NSTX Project Manager

| Revision | Date | TRB | Description of Change |
| --- | --- | --- | --- |

Introduction	1

Central I&C System Requirements	2

1.0 Functions	2

2.0 Configuration Requirements & Essential Features	2

2.1 Location	2

2.2 Design Implementation Philosophy	2

3.0 Performance & Operational Requirements	3

3.1 Baseline Operation	3

3.2 Upgrades	3

Control System Requirements	4

1.0 Functions	4

1.1 Process Control System	4

1.2 Synchronization System	4

1.3 Safety Interlock System	5

1.4 Access Control System	5

1.5 Network System	5

1.6 Control Room Facility	6

2.0 Configuration Requirements & Essential Features	6

2.1 Process Control System	6

2.2 Synchronization System	6

2.3 Safety Interlock System	7

2.4 Access Control System	7

2.5 Network System	7

2.6 Control Room Facility	7

3.0 Performance & Operational Requirements	8

3.1 Baseline Operation	8

3.1.1 Process Control System	8

3.1.2 Synchronization System	9

3.1.3 Safety Interlock System	10

3.1.4 Access Control System	10

3.1.5 Network System	10

3.1.6 Control Room Facility	10

3.2 Upgrades	10

3.2.1 Process Control System	10

3.2.2 Synchronization System	10

3.2.3 Safety Interlock System	10

3.2.4 Access Control System	10

3.2.5 Network System	10

3.2.6 Control Room Facility	10

Data Acquisition System Requirements	10

1.0 Functions	11

1.1 Data Acquisition System	11

2.0 Configuration Requirements & Essential Features	12

2.1 Data Acquisition System	12

3.0 Performance & Operational Requirements	12

3.1 Baseline Operation	12

3.1.1 Data Acquisition System	12

3.2 Upgrades	13

3.2.1 Data Acquisition System	13

List of Tables

CI&C-2.1-1  Central I&C Room Name Cross-Reference	2

CS-2.4-1  Experimental Area Access Controlled Door Locations	7

CS-2.5-1  Network System Link Locations	7

CS-3.1.1-1  Process Control System I/O Requirements	8

CS-3.1.2-1  Definition of Events	9

DA-1.1-1  List of Data Acquisition System Diagnostics	11

DA-3.1.1-1 WBS 4 Baseline Operation Requirements	12

DA-3.1.1-2 WBS 4 Upgrade Operation Requirements	13

List of FIGURES

APPENDIX

LIST OF REFERENCES

Introduction

This System Requirements Document (SRD) defines the design requirements of the Central Instrumentation and Control (I&C) System of the National Spherical Tokamak Experiment (NSTX).

The Central Instrumentation and Control System will provide remote control, monitoring, data acquisition and data management for the various tokamak and diagnostic subsystems during the operation of the NSTX.  The Central I&C System will provide researchers with access to the facility in support of the operation, physics planning, analysis and coordination of experimental objectives.

The Central I&C work package (WBS 6X) scope will include the design, installation, configuration and support for items such as the Process Control System, Synchronization System, Safety Interlock System, Access Control System, Network System, Data Acquisition System, and the design, layout and furnishing of the Control Room Facility.  The Central I&C work package will also develop standards for subsystem hardware and software elements and will provide consulting and coordination of each subsystem's local I&C effort.

A general section covers information which is relevant to the entire WBS element. Individual  subelements of the WBS Central I&C work scope are covered in separate sections, namely:

• WBS 61 Control System

• WBS 62 Data Acquisition System

Figures and Tables are numbered in format X-Y-Z where X=section (i.e. section abbreviation, e.g. CS for Control System), Y=paragraph number, and Z= sequence number within that paragraph.

References to the requirements identified herein are cited in the body of the document using serial numbers preceded by an "R" and are listed in the Appendix."

WBS 6X -  Central I&C System Requirements

1.0 Functions

a.  [R4>] The Central I&C system shall provide all supervisory control and monitoring of the NSTX facility, including:

• Plant Control and Monitoring (asynchronous routine control and monitoring)

• Synchronization System (synchronization of triggered actions from master clock 	events)

• Critical Data Network (high speed synchronous facility-wide network for real time 	control)

• Safety Interlock System (master supervisory control of experiment)

• Access Control System (control and monitoring of access to hazardous areas)

• Data Acquisition System (periodic sampling, acquisition and display of regularly sampled data, and acquisition and display of data sampled and stored by remote devices)[<R4]

2.0 Configuration Requirements & Essential Features

2.1 Location

a.  [R1>] The NSTX machine shall be installed at the PPPL C-site C-cell (formerly occupied by the Princeton Large Torus (PLT)) [<R1].  The NSTX Central I&C System shall be installed at various locations at the PPPL C-site including the CS Building room C201 (formerly the PLT Control Room), the PPPL C-site COB Building room C221E (formerly the DAS Computer Room), and the PPPL C-site CS Building C-cell room 102A (formerly occupied by the Princeton Large Torus (PLT)) with remote interface locations at the PPPL C-site M.G. Building room 101 Motor Generator Room.

b.  Table CI&C-2.1-1 provides a naming cross-reference for room numbers associated with the NSTX Central I&C System.  Central I&C documentation will reference the assigned NSTX names.

TABLE .c.CI&C-2.1-1 Central I&C Room Name Cross-Reference;

2.2 Design Implementation Philosophy

a.  The design implementation philosophy for the Central I&C System shall be to employ only commercially-available off-the-shelf hardware and software.

3.0 Performance & Operational Requirements

3.1 Baseline Operation

a.  The Central I&C System shall accommodate the following baseline pulse repetition period and operating life requirements as defined in the General Requirements Document.  [R10>] The baseline NSTX machine shall be designed for a pulse repetition period of 300 seconds and a maximum of 100 pulses per 24 hour period.  The NSTX machine shall be designed to operate for a period of 10 years.  NSTX operation shall be assumed to consist of 100 pulses per day, 5 days per week, 3 weeks per month, 9 months per year, for 10 years (total of 135,000 pulses) [<R10].

3.2 Upgrades

a.  The Central I&C System shall comply with the following guidance provided in the GRD regarding upgrades.  [R11>] The upgrades described herein are envisioned as possibilities which may or may not be undertaken, depending on experience gained with NSTX operation, and other factors. The baseline design of NSTX should facilitate the upgrades when possible without significant cost impact. As a minimum, the baseline design shall permit eventual upgrade and the upgrade path shall be identified as part of the baseline design process [<R11].

b.  Neutral Beam Injection (NBI) Upgrade:  [R12>] The NSTX design shall consider an upgrade which would place the four existing PBX-M sources on NSTX.  The baseline design for all NSTX components shall identify an upgrade path for the neutral beam upgrade [<R12].  [R2>] The anticipated Neutral Beam Injection (NBI) upgrade will require additional Central I&C System control, data acquisition, and data network capacity [<R2].

c.  Long Pulse Upgrade:  [R13>] The NSTX design shall consider an upgrade which would remove the baseline TF and OH magnets, and place a new TF magnet in the center stack. The NSTX plasma pulse length shall be assumed to be 60 seconds for this upgrade.  The baseline design for all NSTX components shall identify an upgrade path for the long pulse operation [<R13].  [R3>] The anticipated long pulse upgrade will require additional Central I&C long pulse control and data acquisition capability [<R3].

WBS 61 -  Control System Requirements

1.0 Functions

1.1 Process Control System

a.  The NSTX Central I&C process control system shall provide remote control and monitoring of the tokamak subsystems during the operation of the NSTX.  The tokamak subsystems include the AC Power Systems (TF, PF and CHI), MG sets, OH System, Gas Handling System, Auxiliary Systems (vacuum, cooling and bakeout), and Auxiliary Heating Systems.  They are characterized by high reliability requirements, well known operational parameters and routine operation.

b.  [R5>] The Central I&C {process control system} shall provide reference signals to local I&C {process control} systems (provided by responsible WBS elements) for local feedback control, but is not required to close the loop for feedback control of plant processes [<R5].

c.  The process control system must accommodate the sharing of subsystems that will be common to NSTX and PBX-M.

d.  The process control system shall provide engineering consoles in the NSTX Control Room to serve as the user interface to the engineering processes.  The engineering consoles must provide current and historical trending displays, alarm logging, mimic displays, control capabilities, point monitoring and process control system status displays.

1.2 Synchronization System

a.  The Synchronization System shall generate and distribute synchronous events (preprogrammed) to the NSTX subsystems.  Synchronous events shall prescribe a predefined schedule of occurrences to be initiated at preselected times prior to, during, and after the operation of the experiment.

b.  The Synchronization System shall generate and distribute absolute time to the NSTX subsystems.  Absolute time will be used to correlate acquired data, initiate certain preprogrammed events and maintain simultaneity among the subsystems and the Central I&C System.

c.  External systems generate asynchronous events (state change dependent), such as a power supply state change or a plasma disruption, whenever critical or interesting changes occur.  The Synchronization System shall monitor, prioritize, and distribute state dependent asynchronous events to the NSTX subsystems.

d.  The Synchronization System shall provide triggers with a fixed pulse to initiate devices.  Timed gates with programmable delay and pulse width are required to provide enable windows to devices.

e.  The Synchronization System must generate and distribute a shot number that will be counted sequentially to uniquely identify each experiment.

f.  The Synchronization System must generate and distribute synchronized clock pulses to subsystems and the Central I&C System devices to initiate and execute time dependent processes by counting periodically generated clock pulses.

1.3 Safety Interlock System

a.  All NSTX subsystems' equipment must have built-in self protection.  However, the NSTX Safety Interlock System will provide system-wide coordination for personnel and hardware safety.

b.  The Safety Interlock System must provide continuous monitoring, alarming, and logging of critical systems and invoke mitigating action to ensure personnel and hardware protection.

c.  The Safety Interlock System must display subsystem equipment permissives and inter-system hardwired interlock status.  The transition of any subsystem equipment permissive or hardwired interlock must be time tagged -- with time resolution capable of determining the sequence of events -- and presented in the NSTX Control Room.  The Safety Interlock System must operate from the facilities' uninterruptable power system.

d.  The Safety Interlock System must provide a Safety Lockout Device (SLD) to provide a manual means to place hazardous systems in a safe mode.

1.4 Access Control System

a.  The Access Control System must control and monitor personnel entry, via the seven (7) existing doors, to the NSTX experimental areas to ensure personnel safety.

b.  The Access Control System must interface with the Safety Interlock System to ensure personnel safety before machine operation will be permitted.

c.  The Access Control System shall be modeled after the TFTR controlled access system.

d.  The Access Control System must interface with the Safety Lockout Device (SLD) to determine the status of hazardous components monitored by the Safety Interlock System.

1.5 Network System

a.  The Network System shall provide the following networks:

•  General Purpose Network

•  Process Control System Network

•  Data Acquisition System Network

•  Synchronization System Network

•  Critical Data Network

•  Safety Network

b.  The General Purpose Network shall provide a Local Area Network infrastructure for general purpose computing and display systems that will not require high-speed performance.  Items such as desktop computers, printers, and display terminals will generally interface to the General Purpose Network, which shall be part of the existing PPPL Ethernet.  The General Purpose Network shall provide the means for data transfer, inter-system communication, display of data, user interface functions, and provide access to Wide Area Networks (WANs) such as the ESnet and the internet.

c.  The Process Control System Network shall provide a Local Area Network infrastructure for data transfer, inter-system communication, display of data, and user interface functions in support of the Central I&C Process Control System.

d.  The Data Acquisition System Network shall provide a high-speed Local Area Network infrastructure for data transfer, inter-system communication, display of data, and user interface functions in support of the Central I&C Data Acquisition System.

e.  The Synchronization System Network shall provide a high-speed Local Area Network infrastructure to distribute absolute time, synchronous and asynchronous events, triggers, shot number and clock pulses to the Data Acquisition System and Central I&C tokamak subsystems.

f.  [R4>] The Network System shall provide a Critical Data Network to support high speed synchronous facility-wide real time control [<R4].  The Critical Data Network shall be an isolated network to provide security and guarantee bandwidth availability.

g.  The Safety Network shall provide a redundant Local Area Network infrastructure to support the Safety Interlock System and the Access Control System.

1.6 Control Room Facility

a.  The Control Room Facility shall provide a centralized location for researchers to direct and monitor the experimental operation of the NSTX device.

b.  The Control Room layout shall facilitate interaction among experimental physicists and operations personnel to promote an interactive work environment.

2.0 Configuration Requirements & Essential Features

2.1 Process Control System

a.  All engineering subsystem monitoring of normal and abnormal conditions must be reported in the NSTX Control Room.

2.2 Synchronization System

a.  The timing system signal distribution media shall minimize latency.  This would suggest the use of fiber optics as a practical distribution method.  The Synchronization System's hardware and software shall provide a means to accommodate the distribution system's inherent latency so that a "virtual" simultaneity can be achieved at all nodes.  This would suggest the use of adjustable delay circuits for nodes "close" to the central distribution points, or software compensation for latencies which can be quantified.

b.  A user-friendly man-machine interface utilizing menu driven, iconic, graphics screens to configure timing and event information is required.

2.3 Safety Interlock System

a.  All critical Safety Interlock System components must be monitored to detect malfunctions, and automatically tested to verify operational readiness.  The system must be designed to withstand any single point of failure.

2.4 Access Control System

a.  A fail safe electrical design must prevent machine operation should a single point of failure occur.

b.  The Access Control System must operate from the facilities' uninterruptable power system.

c.  The locations of the seven (7) existing doors that provide access to the NSTX experimental area are listed in Table CS-2.4-1.

TABLE .c.CS-2.4-1  Experimental Area Access Controlled Door Locations;

2.5 Network System

a.  The six networks of the Network System shall connect the C-Site facilities as defined in Table CS-2.5-1.

TABLE .c.CS-2.5-1  Network System Link Locations;

2.6 Control Room Facility

a.  The NSTX Control Room shall be installed in the location previously occupied by the PLT Control Room [R6].

3.0 Performance & Operational Requirements

3.1 Baseline Operation

3.1.1 Process Control System

a.  Four (4) color engineering consoles shall be provided in the NSTX Control Room to serve as the user interface to the engineering processes.  Each console display shall

measure a minimum of 19" diagonal and include a keyboard and a point-and-click device to accept user input.

b.  Trended process control monitor data must be maintained on-line for 30 days to support historical trend display.  After 30 days, data shall be stored off-line for archival purposes.

c.  The NSTX process control system will need to support an estimated 1405 I/O points as outlined in Table CS-3.1.1-1.  Each I/O point requires a low scan rate (nominally 1 Hz) and is defined by one of the following general categories:

Analog Input ==> The system design must accommodate 4-20 mA, 0 to +5 VDC, 0 to +10 VDC, +/-2.5 VDC, +/-5 VDC, +/-10 VDC, thermocouple, RTD, and strain gauge interfaces.

Analog Output ==> The system design must accommodate 4-20 mA, 0 to +5 VDC, 0 to +10 VDC, +/-2.5 VDC, +/-5 VDC, and +/-10 VDC interfaces.

Digital Input ==> The system design must accommodate TTL, contact, +5 VDC, +12 VDC and +24 VDC interfaces.

Digital Output ==> The system design must accommodate TTL, Form "C" Relay, +5 VDC, +12 VDC and +24 VDC interfaces.

TABLE .c.CS-3.1.1-1  Process Control System I/O Requirements;

3.1.2 Synchronization System

a.  [R9] The Synchronization System must generate the sixteen (16) {synchronous (preprogrammed)} baseline events defined in Table CS-3.1.2-1.

Table .c.CS-3.1.2-1  Definition of Events;

| Name | Definition |
| --- | --- |

| SOP | Start of Pulse (start of power supply energization) |
| --- | --- |

| SOPTF | Start of Pulse TF (start of TF current) |
| --- | --- |

| SOPPF | Start of Pulse PF (start of PF current) |
| --- | --- |

| SOFTF | Start of Flat Top TF |
| --- | --- |

| SOI | Start of Initiation |
| --- | --- |

| EOI | End of Initiation |
| --- | --- |

| SOD | Start of Plasma Discharge |
| --- | --- |

| SOF | Start of Plasma Flat Top |
| --- | --- |

| SOX | Start of X-point |
| --- | --- |

| EOX | End of X-point |
| --- | --- |

| EOF | End of Plasma Flat Top |
| --- | --- |

| EOD | End of Plasma Discharge |
| --- | --- |

| EOFTF | End of Flat Top TF |
| --- | --- |

| EOPPF | End of Pulse PF (end of PF current) |
| --- | --- |

| EOPTF | End of Pulse TF (end of TF current) |
| --- | --- |

| EOP | End of Pulse (end of power supply energization) |
| --- | --- |

In addition to the 16 synchronous events listed above, the Synchronization System shall have a capacity for sixteen (16) additional events to accommodate a total baseline capacity of thirty-two (32) synchronous events.

b.  Absolute time must consist of a time in the format of hh:mm:ss:msec:usec and the date in the format of YY/MM/DD.  The time stamp may be absolute, but must be traceable to Coordinated Universal Time (UTC).  Simultaneity between systems must be less than 10.0 usec.  The absolute time accuracy, with respect to Coordinated Universal Time (UTC) shall be +/- 5 usec.

c.  The delay time to detect and transmit an asynchronous event shall be less than 100 usec.  The Synchronization System shall accommodate a total baseline capacity of thirty-two (32) asynchronous events.

d.  The Synchronization System must provide triggers with a fixed 1 usec pulse to initiate devices.

e.  The shot number format shall conform with the existing ...[TBD if this format must remain the same - details of required format].

f.  Synchronization clock frequencies of 1 MHz or higher must be provided to subsystems and the Central I&C System devices.

3.1.3 Safety Interlock System

3.1.4 Access Control System

a.  The Access Control System shall accommodate multiple access modes designated as "Free" access, "Controlled" access. "Hot" access [TBD if this mode is required for NSTX], and "No" access.

3.1.5 Network System

3.1.6 Control Room Facility

3.2 Upgrades

3.2.1 Process Control System

3.2.2 Synchronization System

3.2.3 Safety Interlock System

3.2.4 Access Control System

3.2.5 Network System

3.2.6 Control Room Facility

a.  Audio/Video for Remote Collaborations

WBS 62 -  Data Acquisition System Requirements

1.0 Functions

1.1 Data Acquisition System

a.  The Data Acquisition System shall gather data for the plasma diagnostics as well as the tokamak systems diagnostics, listed in Table DA-1.1-1, during machine operation.

TABLE .c.DA-1.1-1  List of Data Acquisition System Diagnostics;

b.  The Data Acquisition System shall provide physics consoles in the NSTX Control Room to serve as the man/machine interface to support the physics research effort.  The physics consoles must display waveforms, which are graphical presentations of one or more data sets derived from time-dependent signals.  The waveform types shall be described as fundamental waveforms (single input channel of data that may include

elementary calculations to convert raw data into engineering units), composite waveforms (waveforms that require the results of one or more fundamental waveforms to calculate the resultant waveform), and model dependent waveforms (a waveform derived from a computer model which possibly uses fundamental or composite waveforms as inputs, i.e. TRANSP or SNAP).

c.  The Data Acquisition System must provide some real-time (post-shot) analysis.

d.  The Data Acquisition System must provide a data management structure to storage, catalog and secure experimental results for subsequent retrieval and analysis;  and

e.  Data transport shall be provided via the Network System.

f.  [R7] The design of the I&C system shall facilitate access to archived NSTX data by parties outside of the NSTX control room (e.g. remote collaborators, physicists inside and outside of PPPL) in a read-only mode.

g. [R8>] The Central I&C system shall provide sixteen (16) electrically isolated, general purpose signal channels between the test cell and the control room. These signals shall be displayed in the control room in real-time [<R8].

2.0 Configuration Requirements & Essential Features

2.1 Data Acquisition System

a.  The TFTR data handling resources shall be utilized to the maximum extent for NSTX operational support.

b.  [R20>] The interface between the data highway and the diagnostic device control and data acquisition modules shall be a hybrid that can accommodate existing CAMAC equipment and hardware based on newer standards [<R20].

3.0 Performance & Operational Requirements

3.1 Baseline Operation

3.1.1 Data Acquisition System

a.  Twelve (12) color physics consoles shall be provided in the NSTX Control Room to serve as the user interface to the experimental processes.  Each console display shall measure a minimum of 19" diagonal and include a keyboard and a point-and-click device to accept user input.

b.  [R20>] The tabulated data acquisition signals require sampling rates ranging from 100 Hz to 1 MHz and shall be used to meet NSTX diagnostics data acquisition requirements.

To establish requirements for Central I&C, each Data Acquisition signal is included in one of the following general categories:

Low Speed ==> Data Acquisition signals requiring sample rates >100 Hz and ≤2 KHz.

Moderate Speed ==> Data Acquisition signals  requiring sample rates >2 KHz and ≤100 KHz.

High Speed ==> Data Acquisition signals  requiring sample rates >100 KHz and ≤1 MHz.

The Average Sampling Time for each signal category (per NSTX pulse) is also included in the table below.

TABLE .c.DA-3.1.1-1  WBS 4 Baseline Operation Requirements;

WBS 4 Baseline Data Acquisition Requirements

|  | Number of Signals & Average Sampling Time per Pulse |
| --- | --- |

| NSTX Diagnostics | Low Speed >100Hz & ≤2KHz | AVG SMPL Time (sec/ pulse) | Mod. Speed >2KHz & ≤100 KHz | AVG SMPL Time (sec/ pulse) | High Speed >100 KHz & ≤1MHz | AVG SMPL Time (sec/ pulse) |
| --- | --- | --- | --- | --- | --- | --- |

| Day One Diagnostics | 250 | 1 |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |

| Baseline Diagnostics |  |  | 150 | 1 |  |  |
| --- | --- | --- | --- | --- | --- | --- |

| TOTALS | 250 |  | 150 |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |

[<R20]

c.  [R20>] The Day One and baseline diagnostics are expected to generate approximately 3.2 megabytes (MB) of data for each one-second pulse [<R20].

3.2 Upgrades

3.2.1 Data Acquisition System

a.  [R20>]To establish requirements for Central I&C, each Data Acquisition signal is included in one of the following general categories:

Low Speed ==> Data Acquisition signals requiring sample rates >100 Hz and ≤2 KHz.

Moderate Speed ==> Data Acquisition signals  requiring sample rates >2 KHz and ≤100 KHz.

High Speed ==> Data Acquisition signals  requiring sample rates >100 KHz and ≤1 MHz.

The Average Sampling Time for each signal category (per NSTX pulse) is also included in the table below.

TABLE .c.DA-3.1.1-2 WBS 4 Upgrade Operation Requirements;

WBS 4 Upgrade Data Acquisition Requirements

|  | Number of Signals & Average Sampling Time per Pulse |
| --- | --- |

| NSTX Diagnostics | Low Speed >100Hz & ≤2KHz | AVG SMPL Time (sec/ pulse) | Mod. Speed >2KHz & ≤100 KHz | AVG SMPL Time (sec/ pulse) | High Speed >100 KHz & ≤1MHz | AVG SMPL Time (sec/ pulse) |
| --- | --- | --- | --- | --- | --- | --- |

| Upgrade Diagnostics |  |  | 50 | 5 | 100 | 5 |
| --- | --- | --- | --- | --- | --- | --- |

| TOTALS |  |  | 50 |  | 100 |  |
| --- | --- | --- | --- | --- | --- | --- |

[<R20]

b.  [R20>] The upgrade diagnostics are expected to generate approximately 33.2 MB for each one-second pulse. These estimates are comparable to the values for PBX-M at the end of its most recent operating period. They should be increased by about a factor of five when the NSTX pulse duration is lengthened to five seconds [<R20].