National Spherical Tokamak Experiment

NSTX

SYSTEM DESIGN DESCRIPTION

CENTRAL INSTRUMENTATION & CONTROL (I&C)

NSTX-SDD-6X-027

Revision 0

July 15, 1996

________________________________

Dwight Bashore

WBS 6 Manager

________________________________

Charles Neumeyer

NSTX Project Engineering Manager

________________________________

Masa Ono

NSTX Project Manager

| Revision | Date | TRB | Description of Change |
| --- | --- | --- | --- |

Introduction	1

Central I&C System Design Description	2

1.0 Design Description	2

1.1 System Design Features	2

1.2 Layout	2

1.3 Component Design Features	2

2.0 System Performance	2

2.1 Baseline Operation	2

2.2 Upgrades	3

3.0 Interfaces	3

3.1 Interface Points	3

3.1 Interface Requirements	3

4.0 Design Basis	3

4.1 Standards & Codes	3

4.2 Supporting Analysis	3

4.0 Design Implementation	3

4.1 Prototypes	3

4.2 Mock-ups	4

4.3 Component Procurement and Fabrication	4

4.4 System Assembly, Installation, and Testing	4

Control System Design Description	5

1.0 Design Description	5

1.1 System Design Features	5

1.1.1 Process Control System	5

1.1.2 Safety System	8

1.1.3 Control Room and Cable Tray System	10

1.1.4 Plasma Control System	10

1.2 Layout	10

1.2.1 Process Control System	10

1.2.2 Safety System	10

1.2.3 Control Room and Cable Tray System	11

1.2.4 Plasma Control System	13

1.3 Component Design Features	13

1.3.1 Process Control System	13

1.3.2 Safety System	13

1.3.3 Control Room and Cable Tray System	13

1.3.4 Plasma Control System	13

2.0 System Performance	13

3.0 Interfaces	13

3.1 Interface Points	13

3.1.1 Process Control System	13

3.1.2 Safety System	13

3.1.3 Control Room and Cable Tray System	13

3.1.4 Plasma Control System	13

3.2 Interface Requirements	13

3.2.1 Process Control System	13

3.2.2 Safety System	13

3.2.3 Control Room and Cable Tray System	13

3.2.4 Plasma Control System	13

4.0 Design Basis	13

4.1 Standards & Codes	14

4.1.1 Process Control System	14

4.1.2 Safety System	14

4.1.3 Control Room and Cable Tray System	14

4.1.4 Plasma Control System	14

4.2 Supporting Analysis	14

4.2.1 Process Control System	14

4.2.2 Safety System	14

4.2.3 Control Room and Cable Tray System	14

4.2.4 Plasma Control System	14

5.0 Design Implementation	14

5.1 Prototypes	14

5.1.1 Process Control System	14

5.1.2 Safety System	14

5.1.3 Control Room and Cable Tray System	14

5.1.4 Plasma Control System	14

5.2 Mock-ups	14

5.2.1 Process Control System	14

5.2.2 Safety System	14

5.2.3 Control Room and Cable Tray System	14

5.2.4 Plasma Control System	14

5.3 Component Procurement and Fabrication	14

5.3.1 Process Control System	14

5.3.2 Safety System	14

5.3.3 Control Room and Cable Tray System	14

5.3.4 Plasma Control System	14

5.4 System Assembly, Installation, and Testing	14

5.4.1 Process Control System	14

5.4.2 Safety System	14

5.4.3 Control Room and Cable Tray System	14

5.4.4 Plasma Control System	15

Data Acquisition System Design Description	15

1.0 Design Description	15

1.1 System Design Features	15

1.1.1 Data Acquisition System	15

1.1.2 Synchronization System	16

1.2 Layout	16

1.2.1 Data Acquisition System	16

1.2.2 Synchronization System	16

1.3 Component Design Features	16

1.3.1 Data Acquisition System	16

1.3.2 Synchronization System	16

2.0 System Performance	16

2.0.1 Data Acquisition System	16

2.0.2 Synchronization System	16

3.0 Interfaces	17

3.1 Interface Points	17

3.1.1 Data Acquisition System	17

3.1.2 Synchronization System	17

3.2 Interface Requirements	17

3.2.1 Data Acquisition System	17

3.2.2 Synchronization System	17

4.0 Design Basis	17

4.1 Standards & Codes	17

4.1.1 Data Acquisition System	17

4.1.2 Synchronization System	17

4.2 Supporting Analysis	17

4.2.1 Data Acquisition System	17

4.2.2 Synchronization System	17

5.0 Design Implementation	17

5.1 Prototypes	17

5.1.1 Data Acquisition System	17

5.1.2 Synchronization System	17

5.2 Mock-ups	17

5.2.1 Data Acquisition System	17

5.2.2 Synchronization System	17

5.3 Component Procurement and Fabrication	17

5.3.1 Data Acquisition System	18

5.3.2 Synchronization System	18

5.4 System Assembly, Installation, and Testing	18

5.4.1 Data Acquisition System	18

5.4.2 Synchronization System	18

List of Tables

CS-1.1.1-1  NSTX Subsystems Supported By Central I&C's Process Control System	5

DA-1.1-1  List of Data Acquisition System Diagnostics	15

List of FIGURES

CS-1.1.1-1 NSTX Process Control System Block Diagram..................................7

CS-1.1.2-1 NSTX Safety System Block Diagram.............................................9

CS-1.2.3-1 NSTX Control Room Layout.....................................................12

APPENDIX

LIST OF REFERENCES

Introduction

This System Design Description (SDD) describes the design of the Central Instrumentation and Control (I&C) System of the National Spherical Tokamak Experiment (NSTX), in response to the requirements given in NSTX-SRD-6X-012.

The Central Instrumentation and Control System will provide remote control, monitoring, data acquisition and data management for the various subsystems during the operation of the NSTX.  The Central I&C System will provide researchers with access to the facility in support of the operation, physics planning, analysis and coordination of experimental objectives.

A general section covers information which is relevant to the entire WBS element. Individual  subelements of the WBS Central I&C work scope are covered in separate sections, namely:

• WBS 61 Control System

• WBS 62 Data Acquisition System

Figures and Tables are numbered in format X-Y-Z where X=section (i.e. section abbreviation, e.g. CS for Control System), Y=paragraph number, and Z= sequence number within that paragraph.

References to the requirements identified herein are cited in the body of the document using serial numbers preceded by an "R" and are listed in the Appendix."

WBS 6X -  Central I&C System Design Description

1.0 Design Description

The Central I&C WBS element (6X) includes the design, installation, configuration and support for items such as the Process Control System, Safety System, Data Acquisition System, Synchronization System, the hardware portion of the Plasma Control System and the design, layout and installation of the Control Room and cable tray system.

1.1 System Design Features

a.  [R1>] The NSTX machine will be installed at the NSTX Test Cell (PPPL C-site CS Building C-cell room 102A).  The NSTX Central I&C System will be installed at various locations at the PPPL C-site including the NSTX Control Room (CS Building room C201), the NSTX Computer Room (COB Building room C221E), the NSTX Test Cell (CS Building C-cell room 102A), the Motor Generator Room (M.G. Building room 101), the ESAT Building (Systems Test Building) and the PPLCC (Administration Building Computer Addition room A11D PPL Computer Center. [<R1].

b.  All new hardware and software components specified for the Central I&C System are commercially-available off-the-shelf items [<R2].

c.  [R3>] For purposes of the design of NSTX, it is assumed that D-site equipment associated with TFTR operation is available for use on NSTX, except for equipment which is not readily transferable and does not lead to substantial cost savings.[<R3]

d. [R4>] For purposes of the design of NSTX, it is assumed that any equipment associated with PBX-M operation is not available for use on NSTX unless said equipment can be arranged so as to be available either for NSTX or PBX-M, with a time for transfer between one assignment and another of ≤ 4 hours [<R4].

1.2 Layout

a.  Refer to sections describing individual WBS 6 subelements.

1.3 Component Design Features

a.  Not Applicable

2.0 System Performance

2.1 Baseline Operation

a.  [R5>] The Central I&C System satisfies the following baseline pulse repetition period and operating life requirements as defined in the General Requirements Document.  The baseline NSTX machine is designed for a pulse repetition period of 300 seconds and a maximum of 100 pulses per 24 hour period.  The NSTX machine is designed to operate for a period of 10 years.  NSTX operation will consist of 100 pulses per day, 5 days per week, 3 weeks per month, 9 months per year, for 10 years (total of 135,000 pulses) [<R5].

2.2 Upgrades

2.2.1 CHI Current Sustainment Power Supply Upgrade

a. CHI Current Sustainment Power Supply Upgrade: The Central I&C System design can accommodate the CHI current sustainment power supply (which would required additional power supply equipment to utilize one of the baseline OH power supplies in the CHI circuit), by providing additional control, data acquisition, and data network capacity.

2.2.2 Neutral Beam Injection (NBI) Upgrade

a. [R6>] The Central I&C System design can accommodate an upgrade which would place the four existing PBX-M sources on NSTX by providing additional control, data acquisition, and data network capacity [<R6].

2.2.3 Long Pulse Upgrade

a. [R7>] The Central I&C System design can accommodate an upgrade to remove the baseline TF and OH magnets, and place a new TF magnet in the center stack to obtain a pulse length of 60 seconds by providing additional Central I&C long pulse control and data acquisition capability [<R7].

3.0 Interfaces

3.1 Interface Points

a.  Refer to sections describing individual WBS 6 subelements.

3.1 Interface Requirements

a.  Refer to sections describing individual WBS 6 subelements.

4.0 Design Basis

4.1 Standards & Codes

a. The NSTX Power Systems will be designed, constructed, and installed in compliance with the applicable provisions of the following:

1) PPPL Health & Safety Manual, ES&H-5008

4.2 Supporting Analysis

a.  Refer to sections describing individual WBS 6 subelements.

4.0 Design Implementation

4.1 Prototypes

a.  Refer to sections describing individual WBS 6 subelements.

4.2 Mock-ups

a.  Refer to sections describing individual WBS 6 subelements.

4.3 Component Procurement and Fabrication

a.  Refer to sections describing individual WBS 6 subelements.

4.4 System Assembly, Installation, and Testing

a.  Refer to sections describing individual WBS 6 subelements.

WBS 61 -  Control System Design Description

The Control System WBS element (61) includes the design, installation, configuration and support for the Process Control System, Safety System,  the design, layout and installation of the Control Room and Cable Tray system and the hardware portion of the Plasma Control System.

1.0 Design Description

1.1 System Design Features

1.1.1 Process Control System

a. The Process Control System will make use of the existing PPPL Allen-Bradley Programmable Logic Controller (PLC) Central Processing Units (CPUs), I/O modules, power supplies, I/O chassis assemblies, fiber optic modems, data communications modules, special purpose modules, and specialty interface cables to provide remote control and/or monitoring of the NSTX subsystems listed in Table CS-1.1.1-1.[R8]

TABLE .c.CS-1.1.1-1  NSTX Subsystems Supported By Central I&C's Process Control System;

b.  [R9>] The process control system will provide engineering displays in the NSTX Control Room to serve as the user interface to the engineering processes.  The engineering displays will support current and historical trending, alarm logging, mimic displays, control capabilities, point monitoring and process control system status displays [<R9]  [R10>] Four (4) 20" diagonal color engineering displays, with a keyboard and mouse will be provided [<R10].  The display systems will support the Man-Machine Interface (MMI) software.  New MMI software will be used to benefit from improved ease-of-use and programming efficiencies that will be incorporated by the time the Process Control System programming effort will begin.  For estimating purposes, Allen-Bradley's ControlView

product is specified.  However, competing products will be evaluated and the best product that falls within budget will be procured.

c.  [R11>] Allen-Bradley's Universal Remote I/O network will be employed to service remote I/O locations in the Test Cell, the MG Control Room, and the ESAT Building.  Allen-Bradley's Data Highway Plus network will integrate the four PLC CPUs and the four engineering displays to support data transfer and inter-system communication[<R11].  [R12>] The PLC's Universal Remote I/O network signals will be carried via fiber optic into the Test Cell to meet the 20 kV AC rms electrical isolation requirement [R12].

d.  [R14>] The process control system will accommodate the sharing of subsystems that will be common to NSTX and PBX-M [<R14].  Existing transfer capabilities will be employed whenever they exist.  For example, the MG sets can be configured to receive control from five different control systems (C1 through C5).  PBX-M currently uses C5 and NSTX will assume the position previously used by PLT (C2).

e.  A total of four (4) Allen-Bradley PLC CPUs -- one PLC CPU for each WBS element interfacing to the Process Control System -- will be utilized.  Figure CS-1.1.1-1 NSTX Process Control System Block Diagram summarizes the design configuration and layout.

NSTX Process Control System Block Diagram

Figure CS-1.1.1-1

1.1.2 Safety System

a. The Safety System will make use of the existing D-Site Allen-Bradley Programmable Logic Controller (PLC) Central Processing Units (CPUs), I/O modules, power supplies, I/O chassis assemblies, fiber optic modems, data communications modules, special purpose modules, and specialty interface cables to provide a fully redundant PLC interlocking system.

b.  [R14>] All NSTX subsystems' equipment will have built-in self protection.  However, the NSTX Safety System will provide system-wide coordination for personnel and hardware safety [<R14].  This will be accomplished by redundantly monitoring kirk keys, E-Stops, Safety Lockout Devices (SLDs) and door limit switches with a PLC system to log and report safety status to operations personnel in the NSTX Control Room and react appropriately to unsafe conditions.

c.  [R15>] The Safety System shall operate from an uninterruptable power source to ensure continuous operation [<R15].  Local Rack mounted Uninterruptible Power Supplies will be provided at PLC equipment locations.  [R16>] The Safety System will provide a continuously available user interface to the safety process [<R16] by using two

d.  Two (2) Allen-Bradley PLC CPUs will be utilized.  Figure CS-1.1.2-1 NSTX Safety System Block Diagram summarizes the design configuration and layout.

NSTX Safety System Block Diagram

Figure CS-1.1.2-1

e.  [R15>] A fail safe electrical design will prevent machine operation should a single point of failure occur [<R15].  The system will consist of two entirely independant PLC systems, each monitoring the same safety variables.  Should either system detect a failure, action will be taken to safe affected areas and systems.  Both of the PLC systems must agree that no faults exist before machine operation is permitted.  [R17>] The Safety System will provide monitoring, alarming, and logging of critical systems and invoke mitigating action to ensure personnel and hardware protection [R<R17]

f.  [R18>] The Safety System will inhibit personnel access to the NSTX Test Cell if either the Electrical Safety Lockout Device (ESLD) or the Pneumatic Safety Lockout Device (PSLD) is in an unsafe position [<R18].  The ESLD and the PSLD will be monitored by each of the PLC systems.  If either of the SLDs are in an unsafe position, the PLC will prevent machine operation.  Additionally, the SLD itself will provide a means to place the TFTR Test Cell in a safe mode to permit personnel access.  [R21>] the transition of any subsystem equipment permissive status, inter-system interlock status, ESLD status, PSLD status and access mode status will be time tagged -- with time resolution capable of determining the sequence of events -- and reported to the safety displays.[<R21].

g.  [R19>] The Safety System must control and monitor personnel entry, via the seven (7) existing doors, to the NSTX Test Cell to ensure personnel safety.  The Safety System shall ensure personnel safety before machine operation is permitted [<R19].  This will be accomplished using Kirk Keys and monitoring the door positions.

1.1.3 Control Room and Cable Tray System

a.  Twenty Data Service Outlets (DSOs) will be provided throughout the NSTX Control Room to provide access to PPPL's ethernet and Wide Area Networks such as the ESnet and the Internet.  The DSOs are a modular network interface that can support a variety of standard connection types.

1.1.4 Plasma Control System

a. The Plasma Control System will make use of the existing Digital Plasma Control System, currently on TFTR.  The VME-based system contains a Thermis 10-mp host computer, a real-time SKYbolt I Shamrock computer and various I/O channels to perform real-time plasma positioning feedback control.

1.2 Layout

1.2.1 Process Control System

a.  The Process Control System's engineering operator interface displays will be located in the NSTX Control Room to meet the requirement that [R13>] all engineering subsystem monitoring of normal and abnormal conditions must be reported in the NSTX Control Room [<R13].

1.2.2 Safety System

a.  The Safety System's operator interface displays will be located in the NSTX Control Room to meet the requirement that [R20>] the Safety System's user interface will display subsystem equipment permissive status, inter-system interlock status, ESLD status, PSLD status and access mode status in the NSTX Control Room [<R20].

1.2.3 Control Room and Cable Tray System

a. The Control Room will provide a centralized location for researchers to direct and monitor the experimental operation of the NSTX device.  Furniture will be provided to support the engineering and experimental physics activities in the NSTX Control Room.  Some new furniture, with cable management ducts to route cables and wires, will be provided for half of the Control Room Facility.  Table space and chairs will consist of existing PPPL Steelcase furniture.  Figure CS.1.2.3-1

NSTX Control Room Layout

Figure CS-1.2.3-1

b.  [R22>] A cable tray system is provided to economically and easily route power cables, signal cables and fiber optic cables throughout the NSTX facility [<R22].  Signal Cable Tray will be provided in Test Cell with runs through the MG Building to the ESAT Building to route signal cables and fibers.  A power tray system will be provided in the Test Cell Basement.

c.  Twenty Data Service Outlets (DSOs) will be provided throughout the NSTX Control Room to provide access to PPPL's ethernet and Wide Area Networks such as the ESnet and the Internet.  The DSOs are a modular network interface that can support a variety of standard connection types.

1.2.4 Plasma Control System

1.3 Component Design Features

1.3.1 Process Control System

1.3.2 Safety System

TBD

1.3.3 Control Room and Cable Tray System

1.3.4 Plasma Control System

2.0 System Performance

Details pertaining to System Performance will be added during the Interim and Final Design stages.

3.0 Interfaces

Interface documentation will be added during the Interim and Final Design stages.

3.1 Interface Points

3.1.1 Process Control System

3.1.2 Safety System

3.1.3 Control Room and Cable Tray System

3.1.4 Plasma Control System

3.2 Interface Requirements

3.2.1 Process Control System

3.2.2 Safety System

3.2.3 Control Room and Cable Tray System

3.2.4 Plasma Control System

4.0 Design Basis

Documentation of the Design Basis will be added during the Interim and Final Design stages.

4.1 Standards & Codes

4.1.1 Process Control System

4.1.2 Safety System

4.1.3 Control Room and Cable Tray System

4.1.4 Plasma Control System

4.2 Supporting Analysis

4.2.1 Process Control System

4.2.2 Safety System

4.2.3 Control Room and Cable Tray System

4.2.4 Plasma Control System

5.0 Design Implementation

Details pertaining to Design Implementation will be added during the Interim and Final Design stages.

5.1 Prototypes

5.1.1 Process Control System

5.1.2 Safety System

5.1.3 Control Room and Cable Tray System

5.1.4 Plasma Control System

5.2 Mock-ups

5.2.1 Process Control System

5.2.2 Safety System

5.2.3 Control Room and Cable Tray System

5.2.4 Plasma Control System

5.3 Component Procurement and Fabrication

5.3.1 Process Control System

5.3.2 Safety System

5.3.3 Control Room and Cable Tray System

5.3.4 Plasma Control System

5.4 System Assembly, Installation, and Testing

5.4.1 Process Control System

5.4.2 Safety System

5.4.3 Control Room and Cable Tray System

5.4.4 Plasma Control System

WBS 62 -  Data Acquisition System Design Description

Use additional sections to describe the design features which are specific to the lower level subelements of the WBS.

1.0 Design Description

1.1 System Design Features

1.1.1 Data Acquisition System

a. The Data Acquisition System will make use of the existing PPPL CAMAC controllers, digitizer modules, power supplies, I/O chassis assemblies, fiber optic data communications modules, special purpose modules, and specialty interface cables to provide data acquisition for the NSTX subsystems listed in Table CS-1.1.1-1.

TABLE .c.DA-1.1-1  List of Data Acquisition System Diagnostics;

b.  The existing PPPL VAX Cluster will be used to provide a data management structure to store, catalog and secure experimental results for subsequent retrieval and analysis.

c.  The existing VMS Graphics Display System (VGDS) will be used to generate waveforms.

d.  The Central I&C system will provide sixteen (16) electrically isolated, general purpose signal channels between the test cell and the control room.  Sixteen Dymec, Inc analog fiber optic transmitter/receiver pairs will be employed.

1.1.2 Synchronization System

a. The Synchronization System will make use of the existing TFTR Facility Clock System to synchronize data acquisition.  An existing CAMAC 401 Clock Encoder module will be used to generate synchronous events (preprogrammed) to the NSTX subsystems.  Existing CAMAC 404A Decoder Modules monitor the encoded timing signal to trigger timing modules and other special purpose hardware.

b.  The TFTR Facility Clock System can accommodate fiber optic transmission to meet electrical isolation requirements at the Test Cell Boundary and provide noise immunity between the MG Building, ESAT Building and the Control/Computer Rooms.

1.2 Layout

1.2.1 Data Acquisition System

1.2.2 Synchronization System

1.3 Component Design Features

1.3.1 Data Acquisition System

1.3.2 Synchronization System

2.0 System Performance

2.0.1 Data Acquisition System

a.  The Dymec, Inc analog fiber optic transmitter/receiver pairs offer the following performance characteristics for +/- 5V differential signals.

Operating Wavelength (nm)			850

Output Power (dB into 50/125-micron fiber)	-18

Analog Bandwidth (MHz)			1

Signal/Noise Ratio (in 1-Hz bandwidth)	55

Optical Interface				SMA, ST

Electrical Interface				AC

2.0.2 Synchronization System

a.  It is anticipated that the TFTR CAMAC Facility Clock system applied at the NSTX facility can provide 10.0 microsecond simultaneity of data acquisition.

b.  The 401 Clock Encoder Module can generate 32 preprogrammed events.  However, the current 404A Decoder modules only detect 16 events, one is defined as E-Stop.

3.0 Interfaces

Interface documentation will be added during the Interim and Final Design stages.

3.1 Interface Points

3.1.1 Data Acquisition System

3.1.2 Synchronization System

3.2 Interface Requirements

3.2.1 Data Acquisition System

3.2.2 Synchronization System

4.0 Design Basis

Documentation of the Design Basis will be added during the Interim and Final Design stages.

4.1 Standards & Codes

4.1.1 Data Acquisition System

4.1.2 Synchronization System

4.2 Supporting Analysis

4.2.1 Data Acquisition System

4.2.2 Synchronization System

5.0 Design Implementation

Details pertaining to Design Implementation will be added during the Interim and Final Design stages.

5.1 Prototypes

5.1.1 Data Acquisition System

5.1.2 Synchronization System

5.2 Mock-ups

5.2.1 Data Acquisition System

5.2.2 Synchronization System

5.3 Component Procurement and Fabrication

5.3.1 Data Acquisition System

5.3.2 Synchronization System

5.4 System Assembly, Installation, and Testing

5.4.1 Data Acquisition System

5.4.2 Synchronization System