National Spherical Torus Experiment

NSTX

SYSTEM REQUIREMENTS DOCUMENT

POWER SYSTEMS

NSTX-SRD-5X-019

Revision 0

August 5, 1997

________________________________

Raki Ramakrishnan

WBS 5 Manager

________________________________

Charles Neumeyer

NSTX Project Engineering Manager

________________________________

Masa Ono

NSTX Project Manager

| Revision | Date | TRB | Description of Change |
| --- | --- | --- | --- |

| 0 | 8/5/97 |  | First Issue |
| --- | --- | --- | --- |

Introduction	1

General Power System Requirements	2

1.0 Functions	2

2.0 Configuration Requirements & Essential Features	2

3.0 Performance & Operational Requirements	2

3.1 Baseline Operation	2

3.2 Upgrades	3

3.3 Pulse Repetition Period & Operating Life	4

AC Power System Requirements	5

1.0 Functions	5

1.1 Specific Functions of the Experimental AC Power System	5

1.2 Specific Functions of the Auxiliary Systems AC Power System	5

2.0 Configuration Requirements & Essential Features	5

3.0 Performance & Operational Requirements	7

3.1 Composite AC Power Load	7

3.2 Experimental Power Component of Load	9

3.3 Auxiliary Systems Component of Load	11

Toroidal Field (TF) Power Conversion Requirements	13

1.0 Functions	13

2.0 Configuration Requirements & Essential Features	13

3.0 Performance & Operational Requirements	13

3.1 Baseline Operation	13

3.1 Upgrades	15

Poloidal Field/Ohmic Heating (PF/OH) Requirements	16

1.0 Functions	16

2.0 Configuration Requirements & Essential Features	16

3.0 Performance & Operational Requirements	17

3.1 Description of PF/OH Coils	17

Table PF-3.1-3: PF Mutual Inductance Matrix (mH)	18

3.2 Baseline Operation	18

3.2.1 Ampacity Requirements	18

3.2.2 Plasma Scenario Requirements	18

3.2 Upgrades	23

CHI Power Conversion System Requirements	24

1.0 Functions	24

2.0 Configuration Requirements & Essential Features	24

3.0 Performance & Operational Requirements	24

3.1 Baseline Operation	24

3.2 Upgrade Operation	24

3.3 Performance	25

List of Tables

PS-3.1-1: NSTX Plasma Scenarios	2

PS-3.1-2: Inductive Pulse Duty Cycle	3

PS-3.1-3: Partial & Non-Inductive Pulse Duty Cycle	3

PS-3.1-4: Upgrade NSTX Duty Cycle	4

AC-3.1-1: Composite AC Input Power Requirements	8

AC-3.2-1: Experimental Power Loads	10

AC-3.2-1: Experimental Power Loads	12

AC-3.2-2: Experimental Power Energy Consumption	14

TF-3.1-1: TF Requirements	14

TF-3.1-2 TF Performance Requirements	13

PF-2.0-1: Independent PF Circuits	16

PF-3.1-1: PF/OH Coil Geometry	17

PF-3.1-2: PF Conductor Properties	17

PF-3.1-2: PF Circuit Resistances	18

PF-3.1-3: PF Mutual Inductance Matrix (mH)	18

PF-3.2-1: PF Ampacity Requirements	18

PF-3.2-2: PF/OH No Load Voltages	18

PF-3.2-3: PF Measurement and Control Accuracy Requirements	23

CHI-3.3-1 CHI Requirements	25

CHI-3.3-2 CHI Measurement and Control Accuracy Requirements	26

List of FIGURES

AC-2.2.1-1: Equivalent Circuit for Utility Grid Interface	6

PF-3.2-1: OH Current Waveform, Slow Ramp	19

PF-3.2-2: PF/OH Currents, Design Basis Waveform	20

PF-3.2-3: OH Voltage, Design Basis Waveform	21

PF-3.2-4: PF Voltages, Design Basis Waveform	21

PF-3.2-5: PF/OH Power, Design Basis waveform	22

CHI-3.1-1: CHI Capacitor Discharge Current Waveform	26

APPENDIX

LIST OF REFERENCES

Introduction

This System Requirements Document (SRD) defines the requirements and design of the Power Systems (WBS 5X) of the National Spherical Torus Experiment (NSTX).

A general section covers information which is relevant to the entire WBS element. Individual  subelements of the WBS Sample work scope are covered in separate sections, namely:

• WBS 51 AC Power Systems

• WBS 52 Toroidal Field (TF) Power Conversion System

• WBS 53 Poloidal Field/Ohmic Heating (PF/OH) Power Conversion System

• WBS 54 Coaxial Helicity Injection (CHI) Power Conversion System

Figures and Tables are numbered in format X-Y-Z where X=section (i.e. section abbreviation, e.g. PS for Power System), Y=paragraph number, and Z= sequence number within that paragraph.

References to the requirements identified herein are cited in the body of the document using serial numbers preceded by an "R" and are listed in the Appendix.

WBS 5X -  General Power System Requirements

1.0 Functions

The Power Systems WBS element is required to supply and deliver all electrical power to equipment associated with the NSTX.

2.0 Configuration Requirements & Essential Features

a. The NSTX machine shall be installed in the Hot Cell at the PPPL D-site [R1].

3.0 Performance & Operational Requirements

a. The baseline design of NSTX shall not preclude the possibility of the upgrades, and shall facilitate the upgrades whenever possible and cost effective. However, for the Power Systems, none of the upgrade features are required to be incorporated in the baseline design of NSTX [R2].

b. The anticipated upgrades include the following [R2]:

• EC start-up upgrade

• CHI current sustainment power supply

• addition of neutral beam injection (NBI) up to two beam lines

• long pulse operation (with center stack replacement)

3.1 Baseline Operation

Baseline:

a. Baseline NSTX operation involves five basic scenarios, as listed in Table PS-3.1-1. [R4]:

Table PS-3.1-1: NSTX Plasma Scenarios

| SCENARIO | START-UP | SUSTAINMENT | CONFIGURATION |
| --- | --- | --- | --- |

| I | OH | OH | ND, DN |
| --- | --- | --- | --- |

| II | CHI |  | SN |
| --- | --- | --- | --- |

|  |  | OH, HHFWCD | ND, DN |
| --- | --- | --- | --- |

| III | OH (Half-Swing) | OH, HHFWCD | ND, DN, SN |
| --- | --- | --- | --- |

| IV | OH (Half-Swing) |  | ND, DN, SN |
| --- | --- | --- | --- |

|  |  | CHI, HHFWCD | SN |
| --- | --- | --- | --- |

| V | CHI | CHI, HHFWCD | SN |
| --- | --- | --- | --- |

b. Start Up refers to the initiation and drive of plasma current up to flat top. Sustainment refers to the drive of plasma current during flat top. Configuration refers to the plasma shape, either Natural Divertor (ND) (a.k.a. limiter), Double Null (DN) divertor, or Single Null (SN) divertor.

c. Scenario I is fully inductive (initiates and drives plasma current via inductive means only) and requires a full swing of the OH current from maximum positive to maximum

negative value. Scenarios II, III,  and IV are partially inductive (initiate and/or drive plasma current via inductive means). Scenario V is non-inductive (requires no inductive plasma initiation or current drive).

d. As indicated in Table PS-3.1-1, for any scenario one or more sustainment current drive techniques may be used, and one or more configurations may be employed. However, the CHI operation requires a SN plasma configuration.

e. The basic duty cycle of the inductive scenario (Scenario I) is defined in Table PS-3.1-2:

Table PS-3.1-2: Inductive Pulse Duty Cycle

| Parameter | Value | Units | Ref |
| --- | --- | --- | --- |

| Inductive Maximum Pulse Duration | 0.5 | sec | 17 |
| --- | --- | --- | --- |

| Inductive minimum Repetition period | 600 | sec | 18 |
| --- | --- | --- | --- |

f. The basic duty cycle of the partial and non-inductive scenarios (Scenario II, III, IV, and V) is defined in Table PS-3.1-3:

Table PS-3.1-3: Partial and Non-Inductive Pulse Duty Cycle

| Parameter | Value | Units | Ref |
| --- | --- | --- | --- |

| Partial & Non-Inductive Max Pulse Duration | 5 | sec | 19 |
| --- | --- | --- | --- |

| Partial & Non-Inductive Min Repetition Period | 300 | sec | 20 |
| --- | --- | --- | --- |

g. Baseline Heating and Current Drive (H&CD) mix is as follows:

- High Harmonic Fast Wave Current Drive (HHFWCD)

- Coaxial Helicity Injection (CHI)

h. In the baseline configuration the CHI shall provide current drive during the start up phase only, and shall be accomplished via a capacitor bank discharge.

3.2 Upgrades

3.2.1 CHI Current Sustainment Power Supply [R5]

a. The Power Systems design shall consider an upgrade which would provide a power supply to provide CHI current drive sustainment for the full plasma flat top duration.

b. The baseline design for the Power Systems shall identify an upgrade path for the CHI current sustainment mode.

3.2.2 Neutral Beam Injection (NBI) Upgrade [R5]

a. The Power Systems design shall consider an upgrade which would place two TFTR Neutral Beam Injectors on NSTX, each operating in the range of 80 to 110kV with corresponding power to the plasma of 5.33 to 7.33MW, for 5 seconds once every 300 seconds.

b. The baseline design for the Power Systems shall identify an upgrade path for the neutral beam upgrade.

3.2.3 Electron Cyclotron Heating and Current Drive (ECHCD) Upgrade [R5]

a. A 200 kW, 100 msec ECHCD system is targeted for the upgrade. Since the pulse length is short, the most likely power source will be a precharged capacitor bank. Therefore the Power Systems design need not anticipate a high pulsed power load for the ECHD.

3.2.4 Long Pulse Upgrade [R5]

a. The Power Systems design shall consider an upgrade which would remove the baseline TF and OH magnets, and place a new TF magnet in the center stack. The NSTX plasma pulse length shall be assumed to be 60 seconds for this upgrade.

b. The baseline design for the Power Systems shall identify an upgrade path for the long pulse operation. The assumed repetition period shall be as indicated in Table PS-3.2-1, which would (at the same pulse current magnitude as the baseline) result in the same rms current as the baseline.

Table PS-3.2-1: Upgrade NSTX Duty Cycle

| Parameter | Value | Units | Ref |
| --- | --- | --- | --- |

| Upgrade maximum Pulse duration | 60 | sec | 21 |
| --- | --- | --- | --- |

| Upgrade minimum Repetition period | 3600 | sec | 22 |
| --- | --- | --- | --- |

3.3 Pulse Repetition Period & Operating Life

a. The baseline Power Systems shall be designed to produce a maximum of 100 pulses per 24 hour period [R5]

b. The Power Systems shall be designed to operate for a period of 10 years. However, new equipment related to the D-site infrastructure (building and utilities) shall be designed for a 25 year operating life [R5].

c. NSTX operation shall be assumed to consist of 96 pulses per day, 5 days per week, 3 weeks per month, 9 months per year, for 10 years (≈ 130,000 pulses). Non-operating times are available for maintenance [R5].

WBS 51 -  AC Power System Requirements

The AC Power System WBS Element (WBS 51) is divided into two major subelements, namely the Experimental AC Power System (WBS 511, which includes all loads due to TF, PF,  and H&CD systems) and the Auxiliary Systems AC Power System (WBS 512, which includes all NSTX auxiliary or "house" power demands).

1.0 Functions

a. The function of the AC Power System is to provide the source of all electric power required for the NSTX facility.  The AC Power System must establish the connection between the PPPL facility and the local utility network in a fashion which permits the pulsed loading required by the NSTX experiment while maintaining a power source of suitable quality for existing house loads.

1.1 Specific Functions of the Experimental AC Power System

The specific functions of the Experimental AC Power System include:

a. Delivery of power to D-Site 13.8kV S1 bus, from primary AC input terminals of XST-1 to S1 bus.

b. D-site MG equipment, including excitation and cycloconverter drive systems, from S1 bus to variable frequency busses SV1 and SV2.

c. AC distribution from SV1 and SV2 busses to converter transformer primary AC input terminals, including feeds to NB equipment (upgrade).

d. AC distribution from secondary terminals of C-site transformer XQT-1 or XQT-2 to HHFW converter transformer primary AC input terminals.

1.2 Specific Functions of the Auxiliary Systems AC Power System

The specific functions of the Auxiliary Systems AC Power System include:

a. Delivery of power to D-Site 13.8kV S2 bus, from primary AC input terminals of XST-2 to S2 bus.

b. All auxiliary system AC distribution at D-Site, from S2 bus to points of utilization  at 13.8kV, 4.16kV, 480V, 208V, and 120VAC levels.

c. Standby power diesel generator and all associated equipment.

d. UPS systems and all associated equipment.

2.0 Configuration Requirements & Essential Features

a. All input power shall be derived from the 138kV service incoming to the laboratory.

b. The electrical utility service to the Princeton Plasma Physics Laboratory (PPPL) site is a 138 kV transmission line thermally rated at 600 Amp steady state (equivalent to roughly 140 MVA). Present agreements with the local utility, Public Service Electric and Gas (PSE&G) permit PPPL to take a 120 MVA dynamic load without phase correction.

c. The limitation on pulsed loading of the utility service is determined by the regulatory requirements regarding the voltage variation experienced by other customers as a result of the pulsed load. The utility considers a +/-1% variation at the nearest point of connection to other customers to be acceptable.

d. PPPL's pulsing affects other PPPL's loads which derive power from the 138kV system as well, some of which (such as computer systems) are voltage sensitive. For that reason the dynamic voltage variation at PPPL's 138 kV bus (on pulsing) shall be held to +/-3% or better. The composite loads imposed by NSTX and the remainder of PPPL need to be accommodated, as well as fault transients due to short circuits, load sheds etc.

e. The equivalent circuit given in Figure AC-1-1 (100MVA base apparent power) shall be utilized for voltage drop and short circuit calculations [R6].

Figure AC-2.2.1-1: Equivalent Circuit for Utility Grid Interface

g. All auxiliary systems AC power is obtained from the S2 bus at D-site, which is powered by the C-site transformer XST-2.

h. Standard Auxiliary Power Systems services shall be as follows:

• Service voltages (3-phase)		13.8kV, 4.16kV, 480V, 208V

• Service voltages (single phase) 	120V

i. A subset of the Auxiliary Power Systems loads require automatic transfer to the standby (diesel generator) power source in the event of a loss of site power from the 138kV service.

j. A subset of the Auxiliary Power Systems loads require uninterruptable power supplies (UPS).

3.0 Performance & Operational Requirements

3.1 Composite AC Power Load

a. Table AC-3.1-1 describes the requirements for total (composite) input power, as measured at the 138kV utility interface with PPPL, for the maximum upgrade case (see section 3.2).

b. Auxiliary power loads are conservatively estimated based on records of previous D-site operations (see section 3.3).

Table AC-3.1-1: Composite AC Input Power Requirements

| Load | MVA | p.f | MW | MVAR | Ref |
| --- | --- | --- | --- | --- | --- |

| NSTX Exp AC Power (Upgrade) | 17.52 | 0.86 | 15.00 | 9.05 | SRD AC-3.2 |
| --- | --- | --- | --- | --- | --- |

| NSTX Aux Sys AC Power | 8.78 | 0.80 | 7.03 | 5.27 | SRD AC-3.3 |
| --- | --- | --- | --- | --- | --- |

| NSTX D-site MG (between pulses @ 70Hz) | 3.47 | 0.76 | 2.64 | 2.26 | 78,79 |
| --- | --- | --- | --- | --- | --- |

| PPPL House Power (A,B,C,-sites) | 2.25 | 0.80 | 1.80 | 1.35 | 38 |
| --- | --- | --- | --- | --- | --- |

| Max base load | 14.50 | 0.79 | 11.47 | 8.88 |  |
| --- | --- | --- | --- | --- | --- |

| Max Pulsed load | 17.52 | 0.86 | 15.00 | 9.05 |  |
| --- | --- | --- | --- | --- | --- |

| Max load during pulses | 31.97 | 0.83 | 26.47 | 17.93 |  |
| --- | --- | --- | --- | --- | --- |

The following is a description of various details related to the requirements listed in Table AC-3.1-1:

c. Any combination of pulsed load and repetition period with ∫i2(t)dt less than or equal to that described by the nominal loading scenario shall be possible, as long as the repetition period is not less the minimum NSTX repetition period and as long as the peak active and reactive power demands do not exceed the nominal maximum values given in Table AC-3.1-1.

d. Voltage variations and distortion at PPPL's 138 kV bus, under regular operating conditions shall conform to IEEE 519, "IEEE Guide for Harmonic Control and Reactive Compensation of Static Power Converters".

e. Voltage variations at PPPL's 138 kV bus, under unusual and fault conditions (such as load shed or short circuit) shall be limited to less than +/-10%.

f. Harmonic content of the line current at PPPL's 138 kV bus shall not exceed that of a 12 pulse rectifier, i.e.:

harmonic:  				11th    13th    23rd      25th

rms % of fundamental:      		9         7.5       4.5          4

g. Operation at full rating shall not be restricted to any particular time of day.

h. Experimental power loads from other machines at PPPL shall be assumed inactive or not coincident with NSTX. However, the auxiliary systems loads from other experiments at the laboratory shall be considered coincidental, including those due to D-site.

3.2 Experimental Power Component of Load

a. Experimental power shall be taken nominally through one of the two D-site Motor-Generator (MG) units. The only exceptions shall be the HHFWCD system, for which the sources are located at C-site, and the NBI auxiliaries (decel, arc, filament, and magnet supplies) which are fed by the S2 bus at D-site.

b. When the experimental power load is such that the total composite load required by NSTX can be supplied directly by the grid, the configuration of the AC systems shall permit operation directly from the grid without the use of the MG set. Therefore the AC input to the TF, OH, and PF converters, and the AC input to the CHI and NBI equipment, shall each be separately connectable either to the MG set or to the grid. The most likely mode in which the MG set would not be used is during non-inductive NSTX operations when the OH system is not used.

c. Capability for testing of the experimental power equipment when supplied directly from the grid shall be possible within the limits of the grid.

d. Table AC-3.2-1 itemizes and sums the experimental power loads.

Table AC-3.2-1: Experimental Power Loads

| Demand List | MW | Eff | MVA | pf | MW | MVAR | Source | Ref |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| MG (between pulses @ 70Hz) |  |  | 3.5 | 0.76 | 2.6 | 2.3 | S1 | 79,80 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| TF |  |  | 36.0 | 0.28 | 10.0 | 34.6 | MG/S1 | SRD TF-3.1 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| OH |  |  | 100.0 | 0.90 | 90.0 | 43.6 | MG | SRD PF-3.2 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| PF |  |  | 170.0 | 0.20 | 34.0 | 166.6 | MG | SRD PF-3.2 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| CHI |  |  | 20.0 | 0.50 | 10.0 | 17.3 | MG/S1 | SRD CHI-3.3 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| HHFWCD (per source) | 2.00 | 0.50 | 4.6 | 0.87 | 4.0 | 2.3 | Q6 | 27-30 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| NBI Accel (per source) | 2.67 | 0.28 | 10.9 | 0.88 | 9.6 | 5.2 | MG/S1 | 35-37 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| NBI Decel,Arc,Filament,Mag |  |  | 0.6 | 0.80 | 0.5 | 0.4 | S2 | 81,82 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| Baseline Load List | # | MW | MVA | pf | MW | MVAR |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| MG (between pulses @ 70Hz) | 1 |  | 3.5 | 0.76 | 2.6 | 2.3 | S1 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| TF | 1 |  | 36.0 | 0.28 | 10.0 | 34.6 | MG/S1 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| OH | 1 |  | 100.0 | 0.90 | 90.0 | 43.6 | MG |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| PF | 1 |  | 170.0 | 0.20 | 34.0 | 166.6 | MG |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| CHI | 0 |  | 0.0 | 0.50 | 0.0 | 0.0 | MG/S1 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| HHFWCD | 3 | 6 | 13.8 | 0.87 | 12.0 | 6.8 | Q6 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| NBI Accel | 0 | 0 | 0.0 | 0.88 | 0.0 | 0.0 | MG/S1 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| NBI Decel,Arc,Filament,Mag | 0 |  | 0.0 | 0.88 | 0.0 | 0.0 | S2 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| MG (TF+OH+PF+CHI+NBI) |  |  | 279.1 | 0.48 | 134.0 | 244.8 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| Grid (HHFW,NBI Aux) |  |  | 13.8 | 0.87 | 12.0 | 6.8 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| Max Upgrade Load List | # | MW | MVA | pf | MW | MVAR |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| MG (between pulses @ 70Hz) | 1 |  | 3.5 | 0.76 | 2.6 | 2.3 | S1 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| TF | 1 |  | 36.0 | 0.28 | 10.0 | 34.6 | MG/S1 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| OH | 1 |  | 100.0 | 0.90 | 90.0 | 43.6 | MG |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| PF max | 1 |  | 170.0 | 0.20 | 34.0 | 166.6 | MG |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| PF (reduced if direct from grid) | 1 |  | 35.4 | 0.71 | 25.0 | 25.0 | S1 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| CHI | 1 |  | 20.0 | 0.50 | 10.0 | 17.3 | MG/S1 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| HHFWCD | 3 | 6 | 13.8 | 0.87 | 12.0 | 6.8 | Q6 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| NBI Accel | 6 | 16 | 65.5 | 0.88 | 57.6 | 31.1 | MG/S1 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| NBI Decel,Arc,Filament,Mag | 6 |  | 3.8 | 0.80 | 3.0 | 2.3 | S2 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| MG (TF+OH+PF+CHI+NBI) |  |  | 355.8 | 0.57 | 201.6 | 293.2 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| Grid (HHFW,NBI Aux) |  |  | 17.5 | 0.86 | 15.0 | 9.1 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

The following is a description of various details related to the requirements listed in Table AC-3.2-1:

e. PF loads are based on simultaneous operation of all PF coil circuits at their maximum current ratings (see section PF-3.2). Actual load scenarios are much less.

f. For the case when operation is entirely from the grid, peak S1 bus power shall be limited to 120MVA and 50 MVAR.

g. MG loads are based on operation via the MG set with  PF loads and NBI taken via MG.

h. Grid pulsed loads consist of the HHFW and NBI auxiliaries.

i. The ECHCD power during a pulse is assumed to be provided by an energy storage capacitor bank, charged prior to the pulse. Therefore the power consumption during the pulse is zero.

j. Any combination of pulsed load and repetition period with ∫i2(t)dt less than or equal to that described by the nominal loading scenario shall be possible, as long as the repetition period is not less than the minimum NSTX repetition period and as long as the peak active and reactive power demands do not exceed the nominal maximum values given in Table AC-3.2-2.

k. Details of long pulse upgrade loads are TBD.

l. Conservative estimate of the total energy required from the MG set for the TF and PF coils, based on magnetic energy due to the self-inductance of all coils at their maximum current ratings, and the dissipated energy due to all coils at their maximum current and ESW ratings, is given in Table AC-3.2-2.

Table AC-3.2-2: Experimental Power Energy Consumption

| Circuit | Max Current | Lself | Mag Energy | Dissipation | ∑Energy |
| --- | --- | --- | --- | --- | --- |

|  | (kA) | (mH) | (MJ) | (MJ) | (MJ) |
| --- | --- | --- | --- | --- | --- |

| OH | 24.0 | 13.00 | 3.74 | 33.27 | 37.02 |
| --- | --- | --- | --- | --- | --- |

| PF1au | 15.0 | 0.38 | 0.04 | 3.51 | 3.55 |
| --- | --- | --- | --- | --- | --- |

| PF1al | 15.0 | 0.38 | 0.04 | 3.51 | 3.55 |
| --- | --- | --- | --- | --- | --- |

| PF1b | 20.0 | 0.54 | 0.11 | 1.15 | 1.25 |
| --- | --- | --- | --- | --- | --- |

| PF2u | 20.0 | 1.98 | 0.40 | 8.84 | 9.24 |
| --- | --- | --- | --- | --- | --- |

| PF2l | 20.0 | 1.98 | 0.40 | 8.84 | 9.24 |
| --- | --- | --- | --- | --- | --- |

| PF3u | 20.0 | 5.18 | 1.04 | 17.71 | 18.75 |
| --- | --- | --- | --- | --- | --- |

| PF3l | 20.0 | 5.18 | 1.04 | 17.71 | 18.75 |
| --- | --- | --- | --- | --- | --- |

| PF4 | 20.0 | 8.56 | 1.71 | 31.23 | 32.94 |
| --- | --- | --- | --- | --- | --- |

| ∑PF |  |  |  |  | 134.28 |
| --- | --- | --- | --- | --- | --- |

| TF | 35.58 | 4.18 | 2.64 | 42.10 | 44.74 |
| --- | --- | --- | --- | --- | --- |

| ∑Total |  |  |  |  | 179.02 |
| --- | --- | --- | --- | --- | --- |

3.3 Auxiliary Systems Component of Load

Load estimates based on 1996 utility power metering records during TFTR operating months  are summarized in Table AC-3.3-1. Actual loads for NSTX are expected to be less.

Table AC-3.3-1: Auxiliary Power Loads

| Description | MVA | p.f. | MW | MVAR | Ref |
| --- | --- | --- | --- | --- | --- |

| D-site Auxiliary Power (S2 bus) Demand | 8.784 | 0.800 | 7.03 | 5.270 | 39 |
| --- | --- | --- | --- | --- | --- |

WBS 52 -  Toroidal Field (TF) Power Conversion Requirements

1.0 Functions

a. The TF Power Conversion System shall be designed to provide a constant current in the TF magnets during an NSTX discharge based on a reference current input signal provided in real time.

2.0 Configuration Requirements & Essential Features

a. The TF Power Conversion System shall include all equipment necessary to power the TF coils. This shall include all equipment from the AC input power interface through to the DC bus connections to the magnets, converter transformers, thyristor converters, DC cable, DC bus, disconnect switches and bus links, and all associated monitoring, control, and protection equipment.

b. Bus links or other means shall be provided in order that the current in the TF magnets can be driven in either direction. The polarity reversal procedure shall require 4 hours or less [R9]

c. No-load disconnect switches shall be provided to isolate the TF Power Conversion System from the connections to the TF magnets. In addition, no-load grounding switches shall be provided to ground the terminals of the connections to the TF magnets. These switches shall be interlocked with test cell access control [R9].

d. The TF power system equipment shall be equipped with a local control system which shall include provisions for closed loop current control using proportional (P) and integral (I) feedback to effect tracking of reference signals.

e. The TF Power Conversion System shall include protection to avoid the delivery of current which would overheat the TF magnets, assuming that their coolant conditions are nominal [R9].

f. Redundant measurements of TF current shall be provided [R9].

g. The TF power  system  shall be grounded via high resistance connections at the (+) and (-) coil terminals.  A ground fault protection system shall be used in conjunction with the grounding scheme to detect grounds within the TF circuit.

h. The TF power system equipment and bus system external to the test cell shall be totally enclosed so that access can be maintained around the operating equipment without danger to the personnel.

i. Dummy load, and system of bus links permitting connection into TF power system circuit, shall be provided. Load impedance and time constant should be similar to the NSTX TF coils. Load ampacity should permit a brief flat top at full baseline TF current.

3.0 Performance & Operational Requirements

3.1 Baseline Operation

Basic requirements are summarized in Table TF-3.1-1.

Table TF-3.1-1: TF Requirements

| Parameter | Value | Units | Ref |
| --- | --- | --- | --- |

| Major Radius R | 0.85 | m | 39 |
| --- | --- | --- | --- |

| TF Coil # Turns | 36 | turns | 40 |
| --- | --- | --- | --- |

| TF Coil Inductance | 0.004 | henries | 41 |
| --- | --- | --- | --- |

| Max Allowable Equivalent Square Wave | 5.3 | sec | 42 |
| --- | --- | --- | --- |

| TF ∑Inner Leg Resistance @ T0 | 4.6873E-03 | Ω | 43 |
| --- | --- | --- | --- |

| TF ∑Outer Leg Resistance @ T0 | 1.1001E-03 | Ω | 44 |
| --- | --- | --- | --- |

| TF ∑Joint/Flag Resistance @ T0 | 4.8565E-04 | Ω | 45 |
| --- | --- | --- | --- |

| TF B - Baseline Pulse | 0.3000 | Tesla | 46 |
| --- | --- | --- | --- |

| TF Flat Top Duration - Baseline Pulse | 5.00 | sec | 47 |
| --- | --- | --- | --- |

| TF Repetition Period - Baseline Pulse | 300.00 | sec | 48 |
| --- | --- | --- | --- |

| TF B - High Field Pulse | 0.6000 | Tesla | 49 |
| --- | --- | --- | --- |

| TF Flat Top Duration - High Field Pulse | 0.60 | sec | 50 |
| --- | --- | --- | --- |

| TF Repetition Period - High Field Pulse | 300.00 | sec | 51 |
| --- | --- | --- | --- |

| TF B - Long Pulse | 0.3000 | Tesla | 52 |
| --- | --- | --- | --- |

| TF Flat Top Duration - Long Pulse | 60.00 | sec | 53 |
| --- | --- | --- | --- |

| TF Repetition Period - Long Pulse | 3600.00 | sec | 54 |
| --- | --- | --- | --- |

| TF Current Measurement Accuracy | 0.5 | % | 55 |
| --- | --- | --- | --- |

| TF Current Control Accuracy | 0.5 | % | 56 |
| --- | --- | --- | --- |

The following are points of elaboration with regard to Table TF-3.1-1:

a. The Equivalent Square Wave (ESW) is the time duration of a constant current (equal to the current required to produce the required magnetic field) for which the ∫i2(t)dt produces the maximum allowable coil temperature rise under adiabatic conditions. The current waveform in actual operation shall have an ∫i2(t)dt which is less than or equal to that given by the ESW.

b. Current measurement accuracy specification is defined as the absolute value of the difference between the measured value and the actual value as a percentage of the full scale value.

c. The current control accuracy specification corresponds to steady state conditions and is defined as the difference between the measured DC current and the reference current as a percentage of the full scale current, excluding measurement errors.

The derived TF performance requirements are summarized in Table TF-3.1-2.

Table TF-3.1-2 TF Performance Requirements

| Parameter | Value | Units | Ref |
| --- | --- | --- | --- |

| Baseline Pulse Current | 35583.3 | amps |  |
| --- | --- | --- | --- |

| Baseline Pulse ESW | 5.3 | sec | 42 |
| --- | --- | --- | --- |

| Baseline Pulse ∫i^2dt | 6.71E+09 | amp^2-sec |  |
| --- | --- | --- | --- |

| Baseline Pulse Repetition Period | 300.0 | sec | 48 |
| --- | --- | --- | --- |

| Baseline Pulse Irms | 4729.6 | amps |  |
| --- | --- | --- | --- |

| High Field Pulse Current | 71166.7 | amps |  |
| --- | --- | --- | --- |

| High Field Pulse ESW | 1.3 | sec |  |
| --- | --- | --- | --- |

| High Field Pulse ∫i^2dt | 6.71E+09 | amp^2-sec |  |
| --- | --- | --- | --- |

| High Field Pulse Repetition Period | 300.0 | sec |  |
| --- | --- | --- | --- |

| High Field Pulse Irms | 4729.6 | amps |  |
| --- | --- | --- | --- |

| End of Flat Top Coil Resistance | 7.8773E-03 | Ω |  |
| --- | --- | --- | --- |

| Baseline End of Flat Top Power | 10.0 | MW |  |
| --- | --- | --- | --- |

| No Load Voltage | 1.0 | kV |  |
| --- | --- | --- | --- |

| Baseline Flat Top Power Factor | 0.3 | p.u. |  |
| --- | --- | --- | --- |

| Energy per Baseline Pulse | 42.1 | MJ |  |
| --- | --- | --- | --- |

| Long Pulse Current | 35583.3 | amps |  |
| --- | --- | --- | --- |

| Long Pulse ESW | 60.0 | sec | 53 |
| --- | --- | --- | --- |

| Long Pulse ∫i^2dt | 7.60E+10 | amp^2-sec |  |
| --- | --- | --- | --- |

| Long Pulse Repetition Period | 3600.0 | sec |  |
| --- | --- | --- | --- |

| Long Pulse Irms | 4593.8 | amps | 83 |
| --- | --- | --- | --- |

The following are points of elaboration with regard to Table TF-3.1-2:

a. The TF power supply system shall be capable of driving the coil current from zero to full current, regulating the current at the specified flat top value for the specified flat top period, and then driving the current to zero. The ∫i2(t)dt of the resultant waveform shall be within the specified limit.

b. In case of a fault the TF power supply shall shut down in such a way that the maximum ∫i2(t)dt of the pre-fault and post-fault current waveform does not exceed the maximum value given Table TF-1.3-2.

3.1 Upgrades

a. None of the upgrade requirements are imposed on the baseline TF Power Conversion System [R3].

WBS 53 -  Poloidal Field/Ohmic Heating (PF/OH) Requirements

1.0 Functions

a. The PF/OH Power Conversion System shall provide a variable current in the PF and OH magnet circuits  during an NSTX discharge based on a reference voltage or current input signal provided in real time [R10].

2.0 Configuration Requirements & Essential Features

a. The PF/OH Power Conversion System shall include all of the equipment necessary to power the PF coils.  This includes all equipment from the primary terminals of the converter transformers through to the DC bus connections to the magnets, consisting of phase controlled thyristor converters, disconnect switches and bus links, and all associated monitoring, and protection equipment.

b. The PF coils shall be connected in series groups in separate circuits with independent current control as indicated in Table PF-2.0-1 [R9].

Table PF-2.0-1: Independent PF Circuits

| PF Circuit | Coil Grouping |
| --- | --- |

| 1 | OH |
| --- | --- |

| 2 | PF1a, upper |
| --- | --- |

| 3 | PF1a, lower |
| --- | --- |

| 4 | PF1b, lower |
| --- | --- |

| 5 | PF2a, PF2b, upper |
| --- | --- |

| 6 | PF2a, PF2b, lower |
| --- | --- |

| 7 | PF3a, PF3b, upper |
| --- | --- |

| 8 | PF3a, PF3b, lower |
| --- | --- |

| 9 | PF4a, PF4b, PF4c, upper & lower |
| --- | --- |

c. All series coil connections indicted in Table PF-2.0-1 shall result in current flow which is equal in magnitude, and in the same φ direction, in the series connected coils [R9].

d. All PF circuits except for OH and PF3 shall be unipolar during a pulse [R8]. OH bipolarity is required to maximize the available flux for inductive current drive. PF3 bipolarity is required to facilitate the formation of a field null prior to plasma initiation.

e. Bus links or other means shall be provided in order that the current in the PF magnets can be driven in either direction. The polarity reversal procedure shall require 4 hours or less [R8].

f. No-load disconnect switches shall be provided to isolate the PF Power System from the connections to the PF magnets. In addition, no-load grounding switches shall be provided to ground the terminals of the connections to the PF magnets. These switches shall be interlocked with test cell access control [R8].

g. Redundant measurements of each PF current shall be provided [R8].

h. The PF Power Conversion System shall include protection to avoid the delivery of current which would overheat the PF magnets, assuming that their coolant conditions are nominal [R8]

i. The PF Power Conversion System shall include protection to prevent OH coil current and PF1b coil current in the opposite φ direction.

j. Dummy load, and system of bus links permitting connection into PF/OH power system circuits, shall be provided. Load impedance and time constant should be similar to the NSTX PF/OH coils. Load ampacity should permit a brief flat top at full baseline PF/OH current.

3.0 Performance & Operational Requirements

3.1 Description of PF/OH Coils

The PF coils are described by their basic geometry as summarized in Table PF-3.1-1 [R66], and their properties as summarized in Table PF-3.1-2.

Table PF-3.1-1: PF/OH Coil Geometry

| Coil | R (center) | ∆R | Z (center) | ∆Z | Turns | Turn CSA | Fill |
| --- | --- | --- | --- | --- | --- | --- | --- |

|  | (cm) | (cm) | (cm) | (cm) |  | (cm^2) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |

| OH | 13.19 | 4.49 | 106.57 | 213.13 | 482.00 | 1.4139 | 0.7120 |
| --- | --- | --- | --- | --- | --- | --- | --- |

| PF1a | 18.03 | 4.16 | 144.83 | 53.88 | 48.00 | 3.3513 | 0.7177 |
| --- | --- | --- | --- | --- | --- | --- | --- |

| PF1b | 30.48 | 8.48 | 181.88 | 17.13 | 28.00 | 3.3513 | 0.6457 |
| --- | --- | --- | --- | --- | --- | --- | --- |

| PF2a | 79.92 | 16.27 | 193.35 | 6.80 | 14.00 | 5.8528 | 0.7409 |
| --- | --- | --- | --- | --- | --- | --- | --- |

| PF2b | 79.92 | 16.27 | 185.26 | 6.80 | 14.00 | 5.8528 | 0.7409 |
| --- | --- | --- | --- | --- | --- | --- | --- |

| PF3a | 149.45 | 18.64 | 163.35 | 6.80 | 15.00 | 5.8528 | 0.6928 |
| --- | --- | --- | --- | --- | --- | --- | --- |

| PF3b | 149.45 | 18.64 | 155.26 | 6.80 | 15.00 | 5.8528 | 0.6928 |
| --- | --- | --- | --- | --- | --- | --- | --- |

| PF4a | 178.27 | 6.78 | 72.75 | 6.80 | 5.00 | 5.8528 | 0.6349 |
| --- | --- | --- | --- | --- | --- | --- | --- |

| PF4b | 179.46 | 9.15 | 64.66 | 6.80 | 8.00 | 5.8528 | 0.7525 |
| --- | --- | --- | --- | --- | --- | --- | --- |

| PF4c | 180.65 | 11.53 | 56.57 | 6.80 | 9.00 | 5.8528 | 0.6723 |
| --- | --- | --- | --- | --- | --- | --- | --- |

Table PF-3.1-2: PF Conductor Properties

| Parameter | Value | Units | Ref |
| --- | --- | --- | --- |

| Resistivity (20C) | 1.724E-06 | Ω-cm | 60 |
| --- | --- | --- | --- |

| Density | 8.9400 | gm/cc | 61 |
| --- | --- | --- | --- |

| Specific Heat | 0.3860 | J/gm-degC | 62 |
| --- | --- | --- | --- |

| Res Temp Coeff | 0.0041 | 1/degC | 63 |
| --- | --- | --- | --- |

| Initial Temp | 20.0 | degC | 64 |
| --- | --- | --- | --- |

| Initial Temp (OH) | 10.0 | degC | 65 |
| --- | --- | --- | --- |

Based on the coil grouping given in Table PF-2.0-1, the coil geometry given in Table PF-3.1-1, and the PF conductor properties given in Table PF-3.1-2, the PF circuit 20 C resistances are given in Tables PF-3.1-3 [R68], and the mutual inductance matrix is given in Table PF-3.1-4 [R69].

Table PF-3.1-2: PF Circuit Resistances

| Circuit | Resistance |
| --- | --- |

|  | (Ω) |
| --- | --- |

| OH | 9.34E-02 |
| --- | --- |

| PF1au | 2.80E-03 |
| --- | --- |

| PF1al | 2.80E-03 |
| --- | --- |

| PF1b | 2.76E-03 |
| --- | --- |

| PF2u | 4.14E-03 |
| --- | --- |

| PF2l | 4.14E-03 |
| --- | --- |

| PF3u | 8.30E-03 |
| --- | --- |

| PF3l | 8.30E-03 |
| --- | --- |

| PF4 | 1.46E-02 |
| --- | --- |

Table PF-3.1-3: PF Mutual Inductance Matrix (mH)

|  | OH | PF1au | PF1al | PF1b | PF2u | PF2l | PF3u | PF3l | PF4 | Plasma |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| OH | 1.30E+01 | 7.31E-01 | 7.31E-01 | 3.74E-01 | 2.76E-01 | 2.76E-01 | 2.95E-01 | 2.95E-01 | 5.05E-01 | 1.32E-02 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| PF1au | 7.31E-01 | 3.76E-01 | 1.95E-04 | 2.26E-04 | 7.23E-02 | 1.35E-03 | 6.04E-02 | 5.29E-03 | 3.90E-02 | 5.22E-04 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| PF1al | 7.31E-01 | 1.95E-04 | 3.76E-01 | 9.01E-02 | 1.35E-03 | 7.23E-02 | 5.29E-03 | 6.04E-02 | 3.90E-02 | 5.22E-04 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| PF1b | 3.74E-01 | 2.26E-04 | 9.01E-02 | 5.36E-01 | 1.66E-03 | 1.86E-01 | 6.61E-03 | 1.01E-01 | 4.93E-02 | 4.96E-04 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| PF2u | 2.76E-01 | 7.23E-02 | 1.35E-03 | 1.66E-03 | 1.98E+00 | 1.03E-02 | 7.31E-01 | 4.11E-02 | 3.08E-01 | 2.68E-03 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| PF2l | 2.76E-01 | 1.35E-03 | 7.23E-02 | 1.86E-01 | 1.03E-02 | 1.98E+00 | 4.11E-02 | 7.31E-01 | 3.08E-01 | 2.68E-03 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| PF3u | 2.95E-01 | 6.04E-02 | 5.29E-03 | 6.61E-03 | 7.31E-01 | 4.11E-02 | 5.18E+00 | 1.66E-01 | 1.31E+00 | 9.32E-03 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| PF3l | 2.95E-01 | 5.29E-03 | 6.04E-02 | 1.01E-01 | 4.11E-02 | 7.31E-01 | 1.66E-01 | 5.18E+00 | 1.31E+00 | 9.32E-03 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| PF4 | 5.05E-01 | 3.90E-02 | 3.90E-02 | 4.93E-02 | 3.08E-01 | 3.08E-01 | 1.31E+00 | 1.31E+00 | 8.56E+00 | 3.45E-02 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| Plasma | 1.32E-02 | 5.22E-04 | 5.22E-04 | 4.96E-04 | 2.68E-03 | 2.68E-03 | 9.32E-03 | 9.32E-03 | 3.45E-02 | 9.77E-05 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

3.2 Baseline Operation

3.2.1 Ampacity Requirements

a. In order to satisfy all NSTX plasma equilibria requirements [R70] the PF/OH circuit ampacities shall be as given in table PF-3.2-1.

Table PF-3.2-1: PF Ampacity Requirements

| Circuit | Max Current | Max ESW | Max ∫i^2(t)dt | Min Trep | Max Irms |
| --- | --- | --- | --- | --- | --- |

|  | (kA) | (sec) | (A^2-sec) | (sec) | (kA) |
| --- | --- | --- | --- | --- | --- |

| OH | 24.0 | 0.525 | 3.02E+08 | 600.0 | 0.71 |
| --- | --- | --- | --- | --- | --- |

| PF1au | 15.0 | 5.0 | 1.13E+09 | 300.0 | 1.94 |
| --- | --- | --- | --- | --- | --- |

| PF1al | 15.0 | 5.0 | 1.13E+09 | 300.0 | 1.94 |
| --- | --- | --- | --- | --- | --- |

| PF1b | 20.0 | 1.0 | 4.00E+08 | 300.0 | 1.15 |
| --- | --- | --- | --- | --- | --- |

| PF2u | 20.0 | 5.0 | 2.00E+09 | 300.0 | 2.58 |
| --- | --- | --- | --- | --- | --- |

| PF2l | 20.0 | 5.0 | 2.00E+09 | 300.0 | 2.58 |
| --- | --- | --- | --- | --- | --- |

| PF3u | 20.0 | 5.0 | 2.00E+09 | 300.0 | 2.58 |
| --- | --- | --- | --- | --- | --- |

| PF3l | 20.0 | 5.0 | 2.00E+09 | 300.0 | 2.58 |
| --- | --- | --- | --- | --- | --- |

| PF4 | 20.0 | 5.0 | 2.00E+09 | 300.0 | 2.58 |
| --- | --- | --- | --- | --- | --- |

3.2.2 Plasma Scenario Requirements

a. In fully inductive modes of NSTX operation, the OH power supply shall:

- precharge the OH coil

- produce sufficient loop voltage to initiate the plasma

- ramp up the plasma in 0.2 ≤ t ≤ 0.4 seconds

- hold the plasma current at flat top for t ≤ 0.5 seconds

- ramp down the plasma in 0.2 ≤ t ≤ 0.4 seconds

- limit the peak current and ∫i^2(t)dt to the values given in Table PF-3.2-1

- provide for a repetition rate ≥ 600 seconds

b. Nominal power supply maximum no load voltage shall be 4kV. However, to ensure plasma initiation under all conditions, 6kV shall be available.

c. Typical fully inductive OH current waveform is given in Figure PF-3.2-1 [R84].

Figure PF-3.2-1: OH Current, Slow Ramp

d. In partial inductive modes of NSTX operation, the OH power supply shall:

- precharge the OH coil

- produce sufficient loop voltage to initiate the plasma

- ramp the OH coil current down to a small value

- limit the peak current  to the value given in Table PF-3.2-1

- limit the ∫i^2(t)dt to 1/2 of the value given in Table PF-3.2-1

- provide for a repetition rate ≥ 300 seconds

e. The PF power supplies shall be capable of operation at the peak currents, ∫i^2(t)dt, and repetition rates given in Table PF-3.2-1.

f. To ensure that all equilibria and scenarios can be supplied, the OH and PF power supplies shall be able to, simultaneously:

- precharge the OH coil

- ramp OH to zero in 0.2 seconds

- ramp all PF currents to their maximum values in 0.2 seconds

- hold at flat top, then ramp down in 0.2 seconds such that each PF circuit 	experiences rated ∫i^2(t)dt

This design basis scenario is depicted in figures PF-3.2-2, -3, and -4.

Figure PF-3.2-2: PF/OH Currents, Design Basis Scenario

Figure PF-3.2-3: OH Voltage, Design Basis Scenario

Figure PF-3.2-4: PF Voltages, Design Basis Scenario

g. The AC power demand due to the above described design basis scenario is given in Figure 3.2-5, assuming no load power supply voltages of 4kV OH, 1kV all PF except PF4 at 2kV.

Figure PF-3.2-4: AC Power, Design Basis Scenario

h. In order to provide sufficient margin for all scenarios as well as additional voltage for control, available no-load voltage in each PF/OH circuit shall be as follows:

Table PF-3.2-2 PF/OH No-Load Voltages

| Circuit | Current Polarity | Nominal No-Load Voltage (kV) | Available No-load Voltage (kV) |
| --- | --- | --- | --- |

| OH | Bipolar | 4 | 6 |
| --- | --- | --- | --- |

| PF1au | Unipolar | 1 | 2 |
| --- | --- | --- | --- |

| PF1al | Unipolar | 1 | 2 |
| --- | --- | --- | --- |

| PF1b | Unipolar | 1 | 2 |
| --- | --- | --- | --- |

| PF2u | Unipolar | 1 | 2 |
| --- | --- | --- | --- |

| PF2l | Unipolar | 1 | 2 |
| --- | --- | --- | --- |

| PF3u | Bipolar | 1 | 1 |
| --- | --- | --- | --- |

| PF3l | Bipolar | 1 | 1 |
| --- | --- | --- | --- |

| PF4 | Unipolar | 2 | 2 |
| --- | --- | --- | --- |

3.2.3 Other Requirements

PF/OH Current measurement and control accuracy requirements are given in Table PF-3.2-2.

Table PF-3.2-2: PF Measurement and Control Accuracy Requirements

| Parameter | Value | Units | Ref |
| --- | --- | --- | --- |

| PF Current Measurement Accuracy | 0.5 | % | 70 |
| --- | --- | --- | --- |

| PF Current Control Accuracy | 0.5 | % | 71 |
| --- | --- | --- | --- |

a. Current measurement accuracy specification is defined as the absolute value of the difference between the measured value and the actual value as a percentage of the full scale value.

b. The current control accuracy specification corresponds to steady state conditions and is defined as the difference between the measured DC current and the reference current as a percentage of the full scale current, excluding measurement errors.

3.2 Upgrades

a. None of the upgrade requirements are imposed on the baseline PF Power Conversion System [R3].

WBS 54 -  CHI Power Conversion System Requirements

1.0 Functions

a. The function of the CHI power system (WBS 54) is to energize the CHI electrodes and impart a poloidal component of current flow which, due to the influence of the toroidal field, results in a toroidal component of plasma current. The power system shall consist of an energy storage capacitor bank with associated charge/discharge equipment along with provision for an upgrade to include an additional power supply to provide current drive after the capacitor bank discharge.

2.0 Configuration Requirements & Essential Features

a. The baseline CHI Power System shall be designed to provide a capacitor bank discharge on to the CHI electrodes, with one electrode connected to the center stack, and one electrode connected to the outer vacuum vessel.

b. Protective features shall be included to prevent the application of excess voltage to the electrodes associated with the center stack. Instantaneous voltage limit shall be 2.0kV.

c. Bus links or other means shall be provided in order that the current in the CHI circuit can be driven in either direction. The polarity reversal procedure shall require 4 hours or less.

d. No-load disconnect switches shall be provided to isolate the CHI Power System from the connections to the CHI load circuit. In addition, no-load grounding switches shall be provided to ground the terminals of the connections to the CHI load circuit. These switched shall be interlocked with test cell access control.

e. For purposes of sizing the CHI power system components, the plasma load circuit may be modeled as an inductance of 80µH and a resistance of 7mΩ, into which a current of 50kA shall be discharged in approximately 5mS, and sustained at 20kA for up to 5 seconds in case the upgrade is undertaken [R73-76].

f. Provision shall be made for an upgrade to include a power supply drive following the capacitor bank discharge [R10]. The power supply shall be a one-quadrant thyristor converter (+V, +I) controllable in either of two modes, namely:

- closed loop current control against a time varying reference current

- open loop voltage control against a time varying reference voltage

3.0 Performance & Operational Requirements

3.1 Baseline Operation

a. The CHI capacitor bank discharge shall be designed to provide a 1/4 cycle sinusoidal current waveform with a peak current of 50.0 kA at 5mS [R75].

3.2 Upgrade Operation

a. The CHI current sustainment power supply shall provide a current of 20.0 kA through an equivalent load resistance of 7 mΩ  for the full duration SOD to EOD [R76].

3.3 Performance

a. CHI performance requirements, computed based on a simple LRC circuit, and assuming the use of two parallel TFTR capacitor banks, and two series TFTR current limiting reactors (CLRs) are given in Table CHI 3.3-1.

Table CHI 3.3-1 CHI Requirements

| Parameter | Value | Units | Ref |
| --- | --- | --- | --- |

| Iinject | 50000.0 | amp | 73 |
| --- | --- | --- | --- |

| Isustain | 20000.0 | amp | 74 |
| --- | --- | --- | --- |

| Lp (effective load) | 8.00E-05 | henry | 75 |
| --- | --- | --- | --- |

| Rp (effective load) | 7.00E-03 | Ω | 76 |
| --- | --- | --- | --- |

| Cbank | 9.90E-03 | farad |  |
| --- | --- | --- | --- |

| Lbank | 8.80E-04 | henry |  |
| --- | --- | --- | --- |

| Nbank | 2 |  |  |
| --- | --- | --- | --- |

| Lclr | 2.65E-04 | henry |  |
| --- | --- | --- | --- |

| Rclr | 1.00E-03 | Ω |  |
| --- | --- | --- | --- |

| Nclr | 2 |  |  |
| --- | --- | --- | --- |

| Cinject | 1.98E-02 | farad |  |
| --- | --- | --- | --- |

| Linject | 1.05E-03 | henry |  |
| --- | --- | --- | --- |

| Rinject | 9.00E-03 | Ω |  |
| --- | --- | --- | --- |

| Omega0 | 219.3 | rad/sec |  |
| --- | --- | --- | --- |

| Vbank | 11870.2 | volt |  |
| --- | --- | --- | --- |

| Ldecay | 6.10E-04 | henry |  |
| --- | --- | --- | --- |

| Rdecay | 9.00E-03 | Ω |  |
| --- | --- | --- | --- |

| Cap Dschg ∫i^2(t)dt (L/R decay to 0) | 9.53E+07 | A^2-sec |  |
| --- | --- | --- | --- |

| Trep | 300.0 | sec |  |
| --- | --- | --- | --- |

| Tsustain | 5.0 | sec |  |
| --- | --- | --- | --- |

| Cap RMS (L/R decay to 0) | 563.6 | amp |  |
| --- | --- | --- | --- |

| Circuit RMS (sustainment mode) | 2642.8 | amp |  |
| --- | --- | --- | --- |

| Vmax (across CHI electrodes) | 977.3 | volt |  |
| --- | --- | --- | --- |

Note: Vmax in Table CHI 3.3-1 refers to the peak voltage during a CHI discharge using the nominal circuit parameters. In practice the voltage could be higher to the extent that the plasma parameters vary. However the voltage shall never exceed 2.0kV.

b. The capacitor discharge and transition to power supply current drive waveform is given in Figure CHI 3.1-1.

Figure CHI 3.3-1:  CHI Capacitor Current Discharge Waveform

c. Miscellaneous performance requirements are given in Table CHI-3.1-2.

Table CHI-3.3-2 CHI Measurement and Control Accuracy Requirements

| Parameter | Value | Units | Ref |
| --- | --- | --- | --- |

| CHI Current Measurement Accuracy | 0.5 | % | 77 |
| --- | --- | --- | --- |

| CHI Current Control Accuracy | 0.5 | % | 78 |
| --- | --- | --- | --- |

d. The CHI power system shall be capable of operation with any set of waveforms and duty cycles characterized by peak current and ∫i2(t)dt within the maximum allowable values.

e. For the power supply upgrade, closed loop current control shall utilize both proportional (P) and integral (I) terms in the control law. The current control error specification corresponds to steady state conditions and is defined as the difference between the measured DC current and the reference current as a percentage of the full scale current, excluding measurement errors.

f. The required current control accuracy shall be achievable with a load of constant inductance and resistance as specified.

g. Voltage measurements shall be made from both bus terminals to ground. Frequency response shall be DC to 1MHz minimum.

h. Current measurement error specification is defined as the difference between the measured value and the actual value as a percentage of the full scale value.

i. The CHI circuit  shall be grounded via the vacuum vessel ground. A ground fault protection system shall be used in conjunction with the grounding scheme to detect grounds within the CHI circuit.

j. The CHI power conversion equipment and bus system shall be totally enclosed so that access can be maintained around the operating equipment without danger to personnel.

| R | Description | Value | Units | Reference |
| --- | --- | --- | --- | --- |

| 1 | Location of NSTX | na | na | GRD sec 1.1.1 |
| --- | --- | --- | --- | --- |

| 2 | Baseline and Upgrade Req'ts | na | na | GRD sec 1.1.2 |
| --- | --- | --- | --- | --- |

| 3 | NSTX Scenario Descriptions | na | na | GRD sec 2.1.2.1 |
| --- | --- | --- | --- | --- |

| 4 | NSTX Upgrade Requirements | na | na | GRD sec 2.1.3 |
| --- | --- | --- | --- | --- |

| 5 | NSTX Operating Lifetime Requirements | na | na | GRD sec 2.1.2.3 |
| --- | --- | --- | --- | --- |

| 6 | PPPL AC Power System Equivalent Circuit | na | na | "Analysis of TPX Pulsing of Utility Grid", TPX Memo 41-940502-PPPL/CNeumeyer-01 |
| --- | --- | --- | --- | --- |

| 7 | TF Configuation & Feature Req'ts | na | na | GRD sec 1.6.2 |
| --- | --- | --- | --- | --- |

| 8 | PF/OH Configuration & Feature Req'ts | na | na | GRD sec 1.6.3 |
| --- | --- | --- | --- | --- |

| 9 | PF Circuit Definition | na | na | GRD sec 1.2.3.1 |
| --- | --- | --- | --- | --- |

| 10 | CHI Configuration & Feature Req'ts | na | na | GRD sec 1.6.4 |
| --- | --- | --- | --- | --- |

| 11 |  |  |  |  |
| --- | --- | --- | --- | --- |

| 12 |  |  |  |  |
| --- | --- | --- | --- | --- |

| 13 |  |  |  |  |
| --- | --- | --- | --- | --- |

| 14 |  |  |  |  |
| --- | --- | --- | --- | --- |

| 15 |  |  |  |  |
| --- | --- | --- | --- | --- |

| 16 |  |  |  |  |
| --- | --- | --- | --- | --- |

| 17 | Inductive Maximum Pulse Duration | 0.50 | sec | GRD sec 2.1.2.1.1 |
| --- | --- | --- | --- | --- |

| 18 | Inductive minimum Repetition period | 600.00 | sec | GRD sec 2.1.2.3.a |
| --- | --- | --- | --- | --- |

| 19 | Partial & Non-Inductive Max Pulse Duration | 5.00 | sec | GRD sec 2.1.2.1.2 |
| --- | --- | --- | --- | --- |

| 20 | Partial & Non-Inductive Min Repetition Period | 300.00 | sec | GRD sec 2.1.2.3.b |
| --- | --- | --- | --- | --- |

| 21 | Upgrade maximum Pulse duration | 60.00 | sec | GRD sec 2.1.3.2.a |
| --- | --- | --- | --- | --- |

| 22 | Upgrade minimum Repetition period | 3600.00 | sec | GRD sec 2.1.3.2.a |
| --- | --- | --- | --- | --- |

| 23 | Operating lifetime | 10 | years | GRD sec 2.1.2.3.c |
| --- | --- | --- | --- | --- |

| 24 | Baseline number of pulses | 130000 | pulses | GRD sec 2.1.2.3.d |
| --- | --- | --- | --- | --- |

| 25 | HHFWCD Power per Source to Plasma | 2.00 | MW | "TPX ICRF Req'ts", S. Ramakrishnan, HSD-3383 TNEA, 2/9/93 |
| --- | --- | --- | --- | --- |

| 26 | HHFWCD Efficiency | 0.50 | p.u. | " |
| --- | --- | --- | --- | --- |

| 27 | HHFWCD Power Factor | 0.87 | p.u. | " |
| --- | --- | --- | --- | --- |

| 28 | HHFWCD Number of Sources | 3.00 | sources |  |
| --- | --- | --- | --- | --- |

| 29 | ECHCD Power per Source to Plasma | 0.20 | MW |  |
| --- | --- | --- | --- | --- |

| 30 | ECHCD Efficiency | 0.25 | p.u. |  |
| --- | --- | --- | --- | --- |

| 31 | ECHCD Power Factor | 0.90 | p.u. |  |
| --- | --- | --- | --- | --- |

| 32 | ECHCD Number of Sources (Upgrade) | 1.00 | sources |  |
| --- | --- | --- | --- | --- |

| 33 | NBI Accel Power per Source to Plasma | 2.67 | MW | S. Ramakrishnan |
| --- | --- | --- | --- | --- |

| 34 | NBI Accel Efficiency | 0.28 | p.u. | S. Ramakrishnan |
| --- | --- | --- | --- | --- |

| 35 | NBI Accel Power Factor | 0.88 | p.u. | S. Ramakrishnan |
| --- | --- | --- | --- | --- |

| 36 | NBI Number of Sources (Upgrade) | 6.00 | sources | GRD sec 1.1.2 |
| --- | --- | --- | --- | --- |

| 37 | D-site S2 Bus Demand | 7.03 | MW | 1996 PPPL PSE&G Bill |
| --- | --- | --- | --- | --- |

| 38 | A,B,C-site Demand | 1.80 | MW | 1996 PPPL PSE&G Bill |
| --- | --- | --- | --- | --- |

| 39 | Major Radius R | 0.854 | m | GRD sec 2.1.1.b |
| --- | --- | --- | --- | --- |

| 40 | TF Coil # Turns | 36 | turns | NSTX-CALC-13-2-0 |
| --- | --- | --- | --- | --- |

| 41 | TF Coil Inductance | 4.176E-03 | henries | NSTX-CALC-13-2-0 |
| --- | --- | --- | --- | --- |

| 42 | Max Allowable Equivalent Square Wave | 5.3 | sec | NSTX-CALC-13-2-0 |
| --- | --- | --- | --- | --- |

| 43 | TF ∑Inner Leg Resistance @ T0 | 4.687E-03 | Ω | NSTX-CALC-13-2-0 |
| --- | --- | --- | --- | --- |

| 44 | TF ∑Outer Leg Resistance @ T0 | 1.100E-03 | Ω | NSTX-CALC-13-2-0 |
| --- | --- | --- | --- | --- |

| 45 | TF ∑Joint/Flag Resistance @ T0 | 4.856E-04 | Ω | NSTX-CALC-13-2-0 |
| --- | --- | --- | --- | --- |

| 46 | TF B - Baseline Pulse | 0.3000 | Tesla | GRD sec 2.1.2.2.b |
| --- | --- | --- | --- | --- |

| 47 | TF Flat Top Duration - Baseline Pulse | 5.00 | sec | GRD sec 2.1.2.2.a |
| --- | --- | --- | --- | --- |

| 48 | TF Repetition Period - Baseline Pulse | 300.00 | sec | GRD sec 2.1.2.3.b |
| --- | --- | --- | --- | --- |

| 49 | TF B - High Field Pulse | 0.6000 | Tesla | GRD sec 2.1.2.2.b |
| --- | --- | --- | --- | --- |

| 50 | TF Flat Top Duration - High Field Pulse | 0.60 | sec | GRD sec 2.1.2.2.b |
| --- | --- | --- | --- | --- |

| 51 | TF Repetition Period - High Field Pulse | 300.00 | sec | GRD sec 2.1.2.3.b |
| --- | --- | --- | --- | --- |

| 52 | TF B - Long Pulse | 0.3000 | Tesla |  |
| --- | --- | --- | --- | --- |

| 53 | TF Flat Top Duration - Long Pulse | 60.00 | sec |  |
| --- | --- | --- | --- | --- |

| 54 | TF Repetition Period - Long Pulse | 3600.00 | sec | GRD sec 2.1.3.2.a |
| --- | --- | --- | --- | --- |

| 55 | TF Current Measurement Accuracy | 0.5 | % |  |
| --- | --- | --- | --- | --- |

| 56 | TF Current Control Accuracy | 0.5 | % |  |
| --- | --- | --- | --- | --- |

| 57 | PF Geometry Description | na |  | NSTX-CALC-13-1-0 |
| --- | --- | --- | --- | --- |

| 58 | Copper 20C Resistivity | 1.7240E-06 | Ω-cm | NSTX-CALC-13-1-0 |
| --- | --- | --- | --- | --- |

| 59 | Copper Density | 8.940 | gm/cc | NSTX-CALC-13-1-0 |
| --- | --- | --- | --- | --- |

| 60 | Copper Specific Heat | 0.386 | J/gm-degC | NSTX-CALC-13-1-0 |
| --- | --- | --- | --- | --- |

| 61 | Copper Resistance Temperature Coeff | 0.0041 | 1/degC | NSTX-CALC-13-1-0 |
| --- | --- | --- | --- | --- |

| 62 | PF Inlet Water Temperature | 20.0 | C | NSTX-CALC-13-1-0 |
| --- | --- | --- | --- | --- |

| 63 | OH Inlet Water Temperature | 10.0 | C | NSTX-CALC-13-1-0 |
| --- | --- | --- | --- | --- |

| 64 | Copper G vs. T | na |  | NSTX-CALC-13-1-0 |
| --- | --- | --- | --- | --- |

| 65 | Copper T vs. G | na |  | NSTX-CALC-13-1-0 |
| --- | --- | --- | --- | --- |

| 66 | PF Circuit Resistances | na |  | NSTX-CALC-13-1-0 |
| --- | --- | --- | --- | --- |

| 67 | PF Mutual Inductance Matrix | na |  | NSTX-CALC-13-1-0 |
| --- | --- | --- | --- | --- |

| 68 | PF Ampacity Requirements | na |  | NSTX-CALC-13-1-0 |
| --- | --- | --- | --- | --- |

| 69 | PF Scenario Analysis | na |  |  |
| --- | --- | --- | --- | --- |

| 70 | PF Current Measurement Accuracy | 0.5 | % |  |
| --- | --- | --- | --- | --- |

| 71 | PF Current Control Accuracy | 0.5 | % |  |
| --- | --- | --- | --- | --- |

| 72 |  |  |  |  |
| --- | --- | --- | --- | --- |

| 73 | CHI Capacitor Discharge Current | 50000.0 | Amp | GRD sec 2.2.2 |
| --- | --- | --- | --- | --- |

| 74 | CHI Power Supply Sustainment Current | 20000.0 | Amp | GRD sec 2.1.3.2 |
| --- | --- | --- | --- | --- |

| 75 | CHI Effective Lp | 8.00E-05 | Henry | D. Orvis e-mail 1/31/97 |
| --- | --- | --- | --- | --- |

| 76 | CHI Effective Rp | 7.00E-03 | Ω | D. Orvis e-mail 1/31/97 |
| --- | --- | --- | --- | --- |

| 77 | CHI Current Measurement Accuracy | 0.5 | % |  |
| --- | --- | --- | --- | --- |

| 78 | CHI Current Control Accuracy | 0.5 | % |  |
| --- | --- | --- | --- | --- |

| 79 | MG Idling Power, 70Hz | 2.64 | MW |  |
| --- | --- | --- | --- | --- |

| 80 | MG Power Factor | 0.76 | p.u. |  |
| --- | --- | --- | --- | --- |

| 81 | NBI Decel, Arc, Filament, Mag Power/Source | 0.50 | MW |  |
| --- | --- | --- | --- | --- |

| 82 | NBI Decel, Arc, Filament, Mag p.f. | 0.80 | p.u. |  |
| --- | --- | --- | --- | --- |

| 83 | TF Max Resistance End of Flat Top | 7.877E-03 | Ω |  |
| --- | --- | --- | --- | --- |

| 84 | OH Scenarios | na |  | 72-970129-SMK-01,"Inductive Discharge Scenarios" |
| --- | --- | --- | --- | --- |