National Spherical Torus Experiment

SPECIFICATION

FOR

HIGH TEMPERATURE BAKEOUT SKID

NSTX-SPEC-33-67

Revision 0

August 23, 2000

PREPARED BY:_____________________________

M. Kalish

REVIEWED BY:_____________________________

F. Malinowski

APPROVED BY:_____________________________

W. Blanchard

PRINCETON UNIVERSITY

PLASMA PHYSICS LABORATORY

(PPPL)

P.O. BOX 451

PRINCETON, NJ 08543

609-243-2000

| Revision | Date | TRB | Description of Change |
| --- | --- | --- | --- |
| 0 | 8/23/00 |  | First Issue |

1.0 SCOPE 	3

2.0 APPLICABLE DOCUMENTS 	3

2.1 DRAWINGS & DESIGN DATA 3

2.2 STANDARDS AND CODES 	3

2.3 GENERAL STATEMENT	 4

3.0 REQUIREMENTS 	5

3.1 PERFORMANCE REQUIREMENTS	 5

3.2 EQUIPMENT CHARACTERISTICS & FEATURES	 6

3.3 ENVIRONMENTAL CONDITIONS	 11

4.0 TEST & INSPECTION REQUIREMENTS 	11

4.1 GENERAL REQUIREMENTS	 11

4.2 CALIBRATION	 11

4.3 FUNCTIONALITY 	11

4.4 PRESSURE TESTING 	11

4.5 OPERATIONAL TESTS 	11

4.6 REGULATORY TESTS 	12

5.0 QUALITY ASSURANCE REQUIREMENTS 	12

5.1 INSPECTION/ SURVEILLANCE/AUDIT BY PRINCETON 	12

5.2 SUBCONTRACTOR'S RESPONSIBILITY FOR CONFORMANCE	 12

5.3 CHANGES TO PRINCETON APPROVED DOCUMENTS	 12

5.4 SUBCONTRACTOR QUALITY ASSURANCE PROGRAM 	12

5.5 QUALITY ASSURANCE PROGRAM MANUAL	 13

5.6 QUALITY ASSURANCE PLAN	 13

5.7 MANUFACTURING/ INSPECTION/TEST (MIT) PLAN	 13

5.8 TRAVELERS/PROCESS SHEETS 	13

5.9 ACCEPTANCE INSPECTIONS AND TESTS	 13

5.10 ACCEPTANCE TEST PROCEDURES	 14

5.11 DOCUMENT TRACEABILITY AND RECORDS	 14

5.12 EQUIPMENT/MATERIAL IDENTIFICATION AND STATUS	 14

5.13 CONTROL OF SPECIAL PROCESSES	 14

5.14 DOCUMENT REVIEW, APPROVAL AND CONTROL	 14

5.15 ACCEPTABILITY OF PURCHASED ITEMS AND SERVICES	 14

5.16 NONCONFORMANCES & CORRECTIVE ACTIONS	 15

5.17 CONFIGURATION CONTROL	 15

5.18 CALIBRATION OF TEST AND MEASURING EQUIPMENT	 15

5.19 RELEASE FOR SHIPMENT FORM	 15

5.20 PROCESS HISTORY	 15

5.21 GENERAL PURCHASE ORDER REQUIREMENTS	 16

6.0 DOCUMENTATION 	17

7.0 HANDLING, SHIPPING AND STORAGE 	18

8.0 DELIVERABLES 	18

ATTACHMENTS

I – P&ID

II- DOE Headmark List (Suspect Fastener List)

II - Blank Certificate of Compliance Form

# 1.0 SCOPE

Subcontractor shall supply the High Temperature Bakeout Skids (HTBS) for the National Spherical Torus Experiment (NSTX), including all required labor, materials, fabrication, assembly and factory acceptance inspections and tests, except where specifically noted otherwise.

The HTBS serves to heat and maintain the NSTX internal plasma facing components (PFCs) at an operator adjustable temperature during bakeout operations.

During bakeout operations the HTBS will be operated in conjunction with an existing Heating/Cooling Skid (HCS). The existing HCS serves to raise the base temperature of the NSTX device, along with the PFCs, to a temperature of up to 150oC prior to activating the HTBS. The HTBS acts as a heat source, heating and circulating saturated steam through tubing mounted to the PFCs inside the NSTX vacuum vessel (VV), and thus serves to further heat the PFCs to a temperature of up to 350oC, at which time the HCS switches to a cooling mode in order to limit the temperature of the outer VV to 150oC.

The HTBS includes reversing valves which can be operated via the HTBS skid control system to reverse the sense of the input and output to the NSTX device, so as to reduce temperature differentials.

The HTBS includes a heat exchanger to recover heat from the steam exiting NSTX and transfer same to the inlet side of the system. The HTBS includes an additional heat exchanger to condense the outlet steam (after heat recovery via the first heat exchanger) so that the resulting liquid can be pumped back into the inlet side. The secondary side of the second heat exchanger connects to the existing NSTX component cooling water system for heat removal.

# 2.0 APPLICABLE DOCUMENTS

## 2.1 DRAWINGS & DESIGN DATA

a. 	Equipment shall be provided in conformance with the High Temperature Bakeout System Process & Instrumentation Diagram (P&ID) attached to this specification (Attachment I).

## 2.2 STANDARDS AND CODES

a. 	Materials and manufacturing/test methods used in fabrication of the equipment covered by this specification shall comply with the latest revision, in effect at date of purchase order, of the following currently approved applicable regulations, safety codes, specifications and standards, including applicable technical definitions as acknowledged and accepted in industry:

ASME (American Society of Mechanical Engineers)

• Boiler & Pressure Vessel Code

Section II		Materials

Section V		Noondestructive Examination

Section VIII		Pressure Vessels, Division I

Section IX		Welding and Brazing Qualifications

• B31.1  Power Piping

• Other ASME standards as referenced in this specification and applicable codes and standards.

ASTM (American Society for Testing & Materials)

• Applicable ASTM standards as referenced in this specification

NFPA (National Fire Protection Association)

• National Electric Code (NEC) 		NFPA No. 70

ANSI (American National Standards Institute)

• National Electrical Safety Code (NESC)	ANSI C2

Occupational Safety and Health Act (OSHA)

• Title 29 CFR 1910 Subpart S - Electrical

• Title 29 CFR 1926 Subpart K, Subpart V - Electrical

b. 	The above Standards and Codes set forth the minimum requirements.  They may be exceeded by Subcontractor if in Subcontractor’s judgment, superior or more economical designs or materials are available.

## 2.3 GENERAL STATEMENT

Subcontractor agrees, represents and warrants that all services, designs, equipment and material sold or otherwise provided to PPPL by Subcontractor comply with applicable:

- Federal, State and Local laws, regulations and codes, and

- All applicable specifications and standards including those specified above in effect at the date of order placement.

Subcontractor shall provide PPPL with a Certificate of Compliance identifying the codes, standards and regulations complied with, and any exceptions taken, in the design and fabrication of deliverable items.

# 3.0 REQUIREMENTS

## 3.1 PERFORMANCE REQUIREMENTS

### 3.1.1 High Temperature Bakeout Skid (HTBS)

a. The HTBS will generate and circulate superheated steam through the PFC system in accordance with the performance requirements given in Table 3.1.1-1.

Table 3.1.1-1: High Temp. Bakeout Skid Performance Requirements

| Requirement | Value | Units |
| --- | --- | --- |
| Steam Mass Flow | 2000 | lbs/hr |
| Steam Outlet Temperature | 475 | oC |
| Steam Outlet Pressure, Maximum | 150 | psig |

b. Anticipated process parameters are indicated on the P&ID.  Subcontractor shall design the HTBS to perform under the conditions indicated thereon, or other conditions which still accomplish the flow and pressure through the NSTX device as required per Table 3.1.1-1. Subcontractor shall provide an analysis of the process parameters anticipated for the HTBS and all other calculations for PPPL review and approval.

### 3.1.2 General

a. Equipment shall be designed for a 10 year life.

b. Equipment shall be designed to operate in the bakeout mode 10 times per year, 48 hours ramp up time, 24 hours hold time, and 24 hours ramp down time (total of 960 hours per year). When not operating the system is disconnected from NSTX, and all remnant liquids can be drained/purged.  Vent and Drain ports are to be provided at appropriate high and low points in the system.

c. Reversing valves shall be designed to handle cycling at a rate of once every 5 minutes.  Reversing valves are to be remotely and automatically actuated with an adjustable cycling rate.

d. Material for pressure retaining components is to be Grade 304 Stainless Steel.  Use of carbon steel components may be acceptable under some circumstances where a large cost saving is actualized but must be reviewed and approved by PPPL.

e. Fabrication and welding of skid components shall be performed in accordance with the requirements of ASME Section VIII and B31.1 Codes as applicable.  All welds shall be visually examined, and subject to nondestructive examination in accordance with the applicable code requirements.

## 3.2 EQUIPMENT CHARACTERISTICS & FEATURES

### 3.2.1 GENERAL

a. Subcontractor shall develop detailed designs for the skid based on the P&ID and requirements given in this specification. Conceptual drawings and Bills of Material for major components shall be submitted by Subcontractor as part of the Technical Proposal package. Detailed fabrication drawings, including assembly drawings, piping and electrical schematics, etc., as well as Bills of Materials, shall be prepared and submitted to PPPL for review and approval prior to Subcontractor procurement and fabrication of items deliverable under this specification.

b. Subcontractor may take exception to certain features called out by the P&ID and this specification in order to effect a technically superior and/or more cost effective design. These shall be submitted by Subcontractor as part of the Technical Proposal package.

### 3.2.2 DESCRIPTION OF COMPONENTS

System must meet requirements specified in section 3.1.  Component specifications may vary from the below descriptions with PPPL approval if basic system requirements are met.  Changes to system are to be support by calculations supplied by the subcontractor.

- Heat Exchanger #1

Heat Exchanger #1 serves to recover heat from the outlet steam flow. Power rating shall be 365kW minimum, and efficiency shall be 60% minimum.

b. 	Steam Generator

Steam Generator converts recirculated water to steam via electrical power input. Power rating shall be 150kW minimum.

- Superheater

Superheater converts steam output from Steam Generator to superheated steam. Power rating shall be 160kW minimum.

- Pressure Regulating Valve

Pressure Regulating Valve shall maintain fixed pressure into NSTX by varying the bypass steam flow. Pressure setting shall be manually controlled between 100 and 150 psig.

- Pressure Relief Valve

Pressure Relief Valve shall provide means for venting the system in case of excess pressure build up, e.g. due to blockage of piping to NSTX or malfunction of reversing valves.  A fitting is to be provided on the discharge of the relief valve for interface with PPPL piping.

- Reversing Valves

Reversing Valves serve to reverse the sense of flow with respect to the NSTX machine. Valves shall be remotely operated via the HTBS control system.  An additional valve shall be provided to allow the system to run in “Bypass Mode” with all flow isolated from NSTX and returned to the skid.

- Heat Exchanger #2

Heat Exchanger #2 serves to condense the outlet steam flow so that it can be pumped by the circulating pump in the liquid state. Power rating shall be 250kW minimum, and efficiency shall be 60% minimum. HTBS shall include a Flow Regulating Valve, adjustable by the HTBS controller, to vary the flow of PPPL component cooling water into heat exchanger #2.  A reservoir with the function of providing continuous head to the circulating pump is to be provided either as part of  Heat Exchanger #2 or as a separate tank.

- Circulating Pump

Circulating Pump serves to pump the liquid condensed by heat exchanger #2. Pump shall be rated to provide a flow of 5 GPM minimum with differential pressure of 100psi.

i. Piping, Valves, and Instrumentation as shown on P&ID

j. Controller

k. Electrical Signal Termination Box

l. Electrical Power Panel and Power Distribution

m. Skid and related accessories

### 3.2.3 GENERAL CONSTRUCTION FEATURES

#### 3.2.3.1 Overall Dimensions

The system shall consist of one skid with maximum dimensions of:

6 ft. width x 9 ft. length x 10 ft. height.

Clearances required for maintenance of the skid and/or replacement of parts are to be presented early in the design process and subject to PPPL approval.

#### 3.2.3.2 Handling Provisions

a. Lifting hooks shall be provided such that skid can be handled via overhead crane.

b. Skid shall include provision for handling via fork lift.

#### 3.2.3.3 Thermal Insulation

All components containing the hot water and steam shall be thermally insulated sufficiently to prevent personnel injury.

#### 3.2.3.4 Identification and Marking

All components, including pumps, motors, valves, pipes, switches, breakers, terminals, and wires shall be labeled in accordance with Subcontractor’s wiring and piping diagrams.

### 3.2.5 ELECTRICAL EQUIPMENT FEATURES

a. Skids shall be equipped to receive 480V, 3 phase AC power via a Non-fusible Square D HD 600V, 3 Pole NEMA disconnect switch (or approved equivalent) with suitable capacity.

b. An incoming circuit breaker shall be provided for each skid, with provision for remote trip.

c. Each skid shall include Power and Control Panel with branch circuit distribution to equipment on skid, and other required relays, controls, starters, interface terminal blocks, etc. Enclosure shall be NEMA 12.

d. All wiring on skid shall be routed in rigid or flexible aluminum conduit as required.

e. Motor starters shall be Square D, Class 8539, NEMA Size 1, with NEMA Type

12 Enclosure, SDA 51 V06; V02 Coil Code, Illuminated Start/Stop Pushbutton with lockout on Stop, 2DPDT additional auxiliary contacts, 3 element factory installed overload, with option for remote control.

f. Skids shall include provision for connection of 4/0 ground cable to PPPL ground bus.

### 3.2.6 INSTRUMENTATION

a. Temperature, pressure, flow, and level measurements shall be provided as indicated on the P&ID over a suitable range, covering start-up conditions to full operating parameters.

- The following measurements shall be displayed at the local HTBS controller:

Flow, pump outlet

Temperature, superheater outlet

Pressure, superheater outlet

Temperature, return from NSTX into HE#1

Pressure, return from NSTX into HE#1

In addition, a 4-20mA output shall be provided for interface with the PPPL control system. Other measurements as indicated on the P&ID may be local readouts.

c. All displays and indicators on the panels shall be clearly and permanently identified and any numeric output shall clearly indicate the units of measurement.

### 3.2.7 CONTROL

a. Temperature Control

Temperature set point of HTBS superheated steam outlet shall be adjustable via a local control panel. Temperature control shall be accomplished by a feedback loop controlling the electric power input to the steam generator and superheater. Actual temperature shall be displayed at the local control panel.

- Pressure Control

Pressure at the steam outlet shall be automatically regulated by the pressure regulating valve.  Actual pressure shall be displayed at the local control panel.

c. Circulating pump control

Circulating pump shall be de-energized when the liquid level in the steam generator drops below a set level.

d. Reversing valve control

Pushbutton shall be provided at the control panel for flow reversal. Flow sense shall toggle from one state to the other upon actuation of the pushbutton on the local control panel. State of valves (normal or reverse) shall be annunciated on the local control panel.  An automatic controller shall be provided so that the valves can be toggled at a preset cycling rate. Provision for remote contact closure from customer control system to toggle valve position, as well as annunciation of state of valves to the PPPL control system, shall be included.

e. Interlocks

Suitable interlocks shall be provided to prevent abnormal operations and unsafe conditions. These shall include:

- Shut down of heaters due to high process temperature trip or high element temperature trip.

- Shut down of heaters and pump due to high process pressure indication

- Shut down of heaters and pump due to low tank level indication

Additional interlocks may be recommended by Subcontractor and approved by PPPL

f. Emergency Stop

Each skid shall be equipped with an Emergency Stop push-button, which shall trip the incoming 480V power, thus shutting down all pumps and electric heaters, and forcing all solenoid operated valves to their safe position. In addition, loss of a PPPL provided 120V AC signal shall provide a remote means for initiating an Emergency Stop. The Emergency Stop input to the skid shall be fused at no more that 1 amp, slow blow.

g. Permissive

Each skid shall accept a PPPL provided contact closure as a Permissive signal. The contact closure shall be required to operate the circulating pumps and heaters.

h. Status

Each skid shall provide one normally open (NO) and one normally closed (NC) contact to PPPL as a status signal indicating that the skid is operational. The contact closure shall indicate that the skid is operating (permissive is present, pumps and heaters are operating).

i. Fault

Each skid shall provide one NO and one NC contact to PPPL as a fault signal indicating that a mis-operation has occurred. Under normal conditions the contacts shall be opposite from shelf state; on fault it shall revert to the shelf state and latch. A manual reset at the skid shall be required.

j. Permissive, Status, Fault, and all other output contacts shall be rated for 24 volts, ac or dc, 500mA, non-inductive load.

## 3.3 ENVIRONMENTAL CONDITIONS

Equipment will be installed in the NSTX Test Cell, which is subject to the following environmental conditions.

Dry Bulb Temperature Range		68 to 72 oF

Humidity Range				30 to 40 % Relative Humidity

Maximum Dew Point Temperature	46 oF

Elevation					Approx. 100 ft above sea level

Magnetic Field				100 gauss

# 4.0 TEST & INSPECTION REQUIREMENTS

## 4.1 GENERAL REQUIREMENTS

a. Subcontractor shall provide all personnel, procedures, materials, equipment, and instruments necessary to perform and record all required examinations and tests, and adequate notification and access to PPPL for witnessing those tests as designated by PPPL.

b. Subcontractor shall furnish and install all temporary test fixtures, flanges, blanking off plates, etc.

## 4.2 CALIBRATION

Subcontractor shall develop procedures, subject to PPPL approval, for calibration of temperature, pressure, flow, and level instrumentation.

## 4.3 FUNCTIONALITY

Subcontractor shall develop procedures, subject to PPPL approval, for testing of basic functionality of all major skid components.

## 4.4 PRESSURE TESTING

Subcontractor shall develop procedures, subject to PPPL approval, for pressure testing of completely assembled skid. The system shall be subjected to hydrostatic testing in accordance with ASME Section 31.1.

## 4.5 OPERATIONAL TESTS

Subcontractor shall propose methods, and develop procedures, subject to PPPL approval, for operational testing of completely assembled skid. Tests shall bring the skid to their rated temperature, pressure, and flow.

## 4.6 REGULATORY TESTS

Subcontractor shall propose methods, and develop procedures, subject to PPPL approval, for code-required testing for pressure vessels and welds.  ASME Code Data Reports shall be provided and each pressure vessel certified and stamped in accordance with ASME Section VIII, UG-115 thru UG-120.

# 5.0 QUALITY ASSURANCE REQUIREMENTS

## 5.1 INSPECTION/ SURVEILLANCE/AUDIT BY PRINCETON

Authorized representatives of PPPL shall have the right at all reasonable times to visit the Subcontractor's premises and those of Subcontractor's suppliers during the performance of the procurement for the purposes of inspection, surveillance, audit and/or obtaining any required information as may be necessary to assure that items or services are being furnished in accordance with specified requirements. Such visits shall be coordinated with the Subcontractor's personnel to minimize interference with the normal operations of said premises.  The Subcontractor shall make available records and documentation necessary for this function and shall provide all reasonable facilities and assistance for the safety and convenience of PPPL representatives in the performance of their duties.  PPPL recognize the Subcontractor's right to withhold information concerning proprietary processes. The Subcontractor agrees to insert the paragraph above in each lower tier procurement issued hereunder.

## 5.2 SUBCONTRACTOR'S RESPONSIBILITY FOR CONFORMANCE

Neither PPPL's review and/or approval of Subcontractor's documents nor PPPL's inspection of Subcontractor's items or services shall relieve the Subcontractor of responsibility for full compliance with requirements of the purchase order/contract.

## 5.3 CHANGES TO PRINCETON APPROVED DOCUMENTS

Revisions or changes by the Subcontractor to documents approved by PPPL shall be reviewed and approved by PPPL prior to use.

## 5.4 SUBCONTRACTOR QUALITY ASSURANCE PROGRAM

The Subcontractor shall establish and maintain an effective Quality Assurance Program and the general criteria to be satisfied by the Program. The objectives of such a program are to assure that the Subcontractor's work meets the required level of quality and is performed in accordance with contractual requirements.

Subcontractor's quality assurance function shall have sufficient authority and independence to identify quality problems, verify conformance of supplied items or services to specified requirements and obtain satisfactory resolution of conflicts involving quality.

## 5.5 QUALITY ASSURANCE PROGRAM MANUAL

The Subcontractor shall submit with the proposal, one (1) copy of its Quality Assurance Program Manual, describing the Subcontractor's quality capability and general approach to quality assurance. The manual shall be subject to PPPL's review and acceptance prior to contract award.

## 5.6 QUALITY ASSURANCE PLAN

Subcontractor shall submit within four weeks of subcontract/purchase order award, three (3) copies of its Quality Assurance Plan, describing the specific quality assurance and quality control procedures and practices to meet the requirements of this particular subcontract/purchase order, for PPPL review and approval.

## 5.7 MANUFACTURING/ INSPECTION/TEST (MIT) PLAN

Subcontractor shall prepare and submit for PPPL review and approval three (3) copies of a Manufacturing/Inspection/Test Plan which identifies parts, sub-assemblies, etc.; shows their integrated flow into end items; and identifies critical manufacturing operations as well as inspections and tests. Preparing the Plan may include developing a flow chart and generating Process Sheets/Shop Travelers, etc.  PPPL reserves the right to designate selected manufacturing, inspection and/or test operations as mandatory "witness" points. Subcontractor shall provide PPPL with five (5) working days notice in advance of such witness points.

## 5.8 TRAVELERS/PROCESS SHEETS

The Subcontractor shall maintain a system of process sheets, shop travelers, or equivalent means, to define the sequence and document the performance of manufacturing, inspection, installation, and test activities. Flow sheets, or equivalent, shall provide for signoff by designated inspection personnel at specified inspection and test points and be traceable to the items.

## 5.9 ACCEPTANCE INSPECTIONS AND TESTS

Each item or service to be delivered to PPPL shall be inspected and tested by the Subcontractor to verify that such items or services meet PPPL's requirements.  Qualified personnel who have not performed or directly supervised the actual work shall perform inspections and tests in accordance with written procedures referencing criteria for acceptance or rejection.  Adequate records shall be maintained and available for PPPL's review.

## 5.10 ACCEPTANCE TEST PROCEDURES

The Acceptance Test Procedures (ATPs), including pass/fail criteria, required to demonstrate conformance to PPPL's requirements shall be prepared by Subcontractor and three (3) copies submitted to PPPL for review and approval at least 10 working days prior to use of such procedures.

## 5.11 DOCUMENT TRACEABILITY AND RECORDS

The Subcontractor shall maintain a system of documentation whereby objective evidence of required operations, inspections, examinations, and tests is systematically compiled, indexed and stored.  Such objective evidence may include "travelers"; and material test, certification, inspection, examination, test and discrepancy reports; which shall be complete, legible, and validated by responsible personnel and shall be traceable to subject items.

## 5.12 EQUIPMENT/MATERIAL IDENTIFICATION AND STATUS

Material and equipment identification shall be maintained throughout the program and be traceable to the records. Status of acceptability shall be readily discernible through the Subcontractor's use of tags, stamps, serial numbers or other positive means.

## 5.13 CONTROL OF SPECIAL PROCESSES

Subcontractor shall use trained and qualified personnel and qualified written procedures in accordance with specified requirements for the performance of certain special processes, including but not limited to, soldering, electronic assembly, brazing, welding, plating, heat treatment, nondestructive examination, etc. Copies of special process procedures shall be available for review by PPPL and submitted to PPPL for review and approval if requested.

## 5.14 DOCUMENT REVIEW, APPROVAL AND CONTROL

The Subcontractor shall provide a system for distribution and control of approved documents and changes thereto. The system shall use procedures, which provide for review and approval of design documents (drawings, specifications, etc.), prior to issuance for use, and for approval and incorporation of changes in a formal and orderly manner. The system shall control obsolete documents to prevent inadvertent use.

## 5.15 ACCEPTABILITY OF PURCHASED ITEMS AND SERVICES

The Subcontractor shall verify conformance of purchased and PPPL-furnished items or services to drawing and specification requirements and shall provide objective evidence of such verifications to PPPL as requested.

## 5.16 NONCONFORMANCES & CORRECTIVE ACTIONS

The Subcontractor shall promptly identify and control nonconforming items or services. Nonconforming items or services shall be positively identified, and segregated where possible, to prevent use. The Subcontractor shall document each nonconformance. The written approval of PPPL is required prior to the use of the nonconforming item or service.

## 5.17 CONFIGURATION CONTROL

Subcontractor shall completely document the configuration of delivered end items or services, using drawing revisions, specification revisions, unique part numbers, or other suitable means.

## 5.18 CALIBRATION OF TEST AND MEASURING EQUIPMENT

Inspections and tests shall be performed using properly calibrated measuring and test equipment. Subcontractor shall have in its possession the necessary equipment to perform the required inspections and tests. Calibration standards shall be traceable to the National Institute for Standards and Technology (NIST) or equivalent. Reference standards shall only be used for calibration and verification unless it is demonstrated that their performance as reference standards has not been invalidated. Subcontractor shall impose these calibration requirements on sub-tier suppliers.

## 5.19 RELEASE FOR SHIPMENT FORM

Subcontractor shall have a signed "Product Quality Certification and Shipping Release" Form to be provided by PPPL's Quality Assurance Representative prior to acceptance of procured items or services for full or partial shipment. PPPL reserves the right to refuse to accept shipments unless accompanied by a signed "Shipping Release" Form.

## 5.20 PROCESS HISTORY

Subcontractor shall provide, at or prior to delivery, PPPL with three (3) copies of the Process History, a compilation of documents, detailing the objective evidence of the acceptability of the work performed. The Process History shall include as a minimum, but not be limited to, the following:

### 5.20.1 CERTIFICATE of COMPLIANCE (CofC)

Subcontractor's C of C identifying the codes, standards and regulations complied with, and any exceptions taken, in the design and fabrication of deliverable items stating that the work performed conforms in every respect to the physical configuration and functional inspection/test requirements. The C of C shall be signed by Subcontractor's Quality Assurance (QA) Manager. One copy to be provided with the Shipping Release request.

### 5.20.2 AS-BUILT CONFIGURATION

The Subcontractor must submit drawings and a listing of the as-built configuration of each delivered item.  The listing may be defined by drawing and revision numbers, unique parts lists or other means of positive identification. Drawings shall be provided as reproducible hard copies (black on white).

### 5.20.3 MATERIAL CERTIFICATIONS

The Subcontractor shall submit copies of Material Test Reports, which represent the actual chemical and physical properties of the material lot/heat number, and provide positive traceability to the material/part/item manufactured. One copy shall be submitted upon Subcontractor acceptance of the material.

### 5.20.4 MANUFACTURING/INSPECTION/TEST DOCUMENTS

Copies of filled in and completed process planning and control documents (travelers, etc.) which verify controlled execution of the required work.

### 5.20.5 INSPECTION & TEST REPORTS

Copies of the original reports of all required inspections, examinations, and tests, properly validated by authorized personnel.  One copy to be provided with the Shipping Release request.

### 5.20.6 DISCREPANCY REPORTS

The Subcontractor must submit copies of discrepancy reports; those affecting form, fit or function.  One copy to be provided with the Shipping Release request.

### 5.20.7 PERSONNEL QUALIFICATION CERTIFICATION

Certification by Subcontractor's Quality Assurance/Control Manager stating that personnel performing or interpreting the results of special processes (i.e., welding, soldering, electronic assembly, brazing, nondestructive examination, etc.) were properly trained and qualified.

## 5.21 GENERAL PURCHASE ORDER REQUIREMENTS

Material(s) and/or product(s), including those components, parts, and materials, which are permanently installed into systems, sub-systems, and/or assemblies, etc. furnished under this purchase order/subcontract, shall be new and unused. Parts and components that have been rebuilt, refurbished, or modified are specifically prohibited unless approved by PPPL in writing.

Subcontractors (Suppliers) found to be supplying any of the following will be reported to the Office of the Inspector General, U.S. Department of Energy.

•	Remanufactured, rebuilt, or used parts represented as new

•	Counterfeit parts (fraudulently labeled or marked with another manufacturer’s name).

•	Misrepresented parts.

### 5.21.1  HIGH STRENGTH FASTENERS

High strength fasteners shall exhibit grade marks and the manufacturer’s identification symbol (headstamp) as specified in the applicable Material Specification. Fasteners having a headmark that is displayed on the attached suspect fastener list will not be accepted

### 5.21.2 ELECTRICAL & MECHANICAL ITEMS

Electrical and Mechanical Items shall exhibit manufacturer’s labels and identification as specified in the referenced specification or in the body of this subcontract.

# 6.0 DOCUMENTATION

Documentation shall be provided as delineated in the following table (one original and one duplicate copy of each document shall be provided unless otherwise specified herein).

| Ref. Section | Item | Due |
| --- | --- | --- |
| 3.1.1 | Analysis of Process Parameters | With proposal |
| 3.1.2.e, 4.1 | Non Destructive Examination Reports, including radiographs | Prior to Shipments |
| 3.1.2.e | Welding Procedures and Procedure Qualification Test Reports | Prior to Fabrication |
| 3.2.1.a | Conceptual Drawings and Bills of Material for major components | With proposal |
| 3.2.1.a | Detailed fabrication drawings and Bills of Materials | Within 4 weeks after contract award |
| 3.2.1.b | Exceptions to P&ID and specification | With proposal |
| 3.2.7.d | Description of protective interlocks | Within 4 weeks after contract award |
| 4.2, 4.3, 4.4, 4.5, 4.6, 5.10 | Acceptance Test Procedures including: hydrostatic testing , magnetic particle, radiographic, visual, and liquid penetrant examination | Within 8 weeks after award & at least 10 working days prior to use |
| 4.6 | ASME Code Data Reports | Prior to Shipment |
| 5.5 | Quality Assurance Manual | With proposal |
| 5.6 | Quality Assurance Plan | Within 4 weeks after award |
| 5.7 | Manufacturing, Inspection & Test Plan | Preliminary with proposal and final within 4 weeks after award & at least 5 working days prior to fabrication |
| 5.19 | Shipping Release Form | Prior to Shipments |
| 5.20 | Process History | At delivery |
| 7.0 | Handling, Shipping & Storage Procedures | If and when requested by PPPL |
| 8.0 | Operations & Maintenance Manuals | At delivery |
| 8.0 | Wiring & Piping Diagrams | Prior to Fabrication |
| Other | Schedule | With Proposal |
| Other | Progress Reports | Weekly from date of order |

# 7.0 HANDLING, SHIPPING AND STORAGE

a. Subcontractor shall control items during handling and shipping and while in storage, including PPPL furnished items, and shall assure that materials and items are adequately protected from damage or deterioration, with special attention to packaging for shipment. Such protection shall include special environmental packaging requirements as specified.  Packaging, shipping and storage procedures shall provide for adequate marking or labeling to clearly and readily identify the items.

b. Procedures may be subject to PPPL review and approval.

# 8.0 DELIVERABLES

Deliverable items shall include the following.

a.  HTBS, including all components listed in section 3.2 of this specification.

- All documentation listed in Section 6.0.

- Wiring and piping diagrams

d.   Printed Operations and Maintenance Manuals

PROCESS & INSTRUMENTATION DIAGRAM (P&ID)

PRINCETON UNIVERSITY PLASMA PHYSIC LABORATORY—PPPL

| PRODUCT QUALITY CERTIFICATION AND SHIPPING RELEASE |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| PROJECT | ITEM DESCRIPTION |  |  | SHIPMENT NUMBER |  |
| PPPL SUBCONTRACT/ ORDER NO. | REV. | ITEM NO. | SUPPLIER REFERENCE NO. | REV. | QTY SHIP |
| SUPPLIER'S CERTIFICATION This is to certify that the products and services identified herein have been produced under a controlled quality assurance program and are in conformance with the procurement requirements including applicable codes, standards and specifications as identified in the above-referenced documents unless noted below. Any supporting documentation will be retained in accordance with the procurement requirements. SIGNED: ____________________________ DATE: __________________________ TITLE: ____________________ COMPANY: _______________________________ |  |  |  |  |  |
| PPPL (AUTHORIZED REPRESENTATIVE) SHIPPING RELEASE This is to certify that evidence supporting the above Supplier's Certification statement has been audited and no product/service nonconformances from procurement requirements have been found unless noted below. This product/service is hereby released for shipment. This section serves as the Quality Assurance release for the above described product for shipment. It does not constitute an acceptance thereof and does not relieve the Vendor, Manufacturer or Contractor of any and all responsibility or obligation imposed by the purchase contract. It does not waive any rights the Purchaser may have under the purchase contract, including the Purchaser's right to reject the above described material upon discovery of any deviations from requirements of the purchase contract, drawings and specifications. |  |  |  |  |  |
| NONCONFORMANCES FROM PROCUREMENT QUALITY REQUIREMENTS: |  |  |  |  |  |
| REMARKS/PRODUCT SERIAL NUMBERS: |  |  |  |  |  |
| BY PPPL QA REPRESENTATIVE (OR DESIGNEE) |  |  |  | DATE |  |