National Spherical Torus Experiment

NSTX

SOFTWARE REQUIREMENTS SPECIFICATION

POWER SUPPLY REAL TIME CONTROLLER

NSTX-SPEC-5X-049

Revision 0

June 1, 1998

Prepared By:

________________________________

C Neumeyer

Reviewed By:

________________________________

S Kaye

NSTX Project Physics Manager

Approved By:

________________________________

S Ramakrishnan

WBS 5 Manager

________________________________

G Oliaro

WBS 6 Manager

| Revision | Date | Description of Change |
| --- | --- | --- |

| 0 | 6/1/98 | Initial Release |
| --- | --- | --- |

1.0 Introduction	5

2.0 Entities to be Monitored and Controlled	5

2.1 Components	5

2.1.1 Motor Generator Sets	5

2.1.2 AC/DC Converters	6

2.1.3 DC Current Transducers	7

2.1.4 Hardwired Control System	7

2.1.5 Other	7

2.2 Circuits		7

2.2.1 Circuit Configurations	7

2.2.2 Listing of NSTX Circuits	9

2.2.3 Utilization of PS in the Circuits	9

2.2.3 Utilization of DCCT in the Circuits	10

2.3 Summary of Input/Output Requirements	11

3.0 Interface with Plasma Real Time Controller (PRTC)	11

3.1 Plasma Control Time Window	11

3.2 Reference Signals Provided in Real Time by the PRTC	11

3.3 PRTC/PSRTC Interface	11

3.3.1 PRTC to PSRTC Signals	11

3.3.2 PSRTC to PRTC Signals	12

4.0 Control Features	12

4.1 Modes, Sub-Modes, States, and Phases of Operation	12

4.1.1 Modes	12

4.1.2 Sub-Modes	12

4.1.3 States	13

4.1.4 Phases	13

4.2 Timing		13

4.3 Functions	14

4.3.1 Power Supply Control Function	14

4.3.1.1 Closed Loop Current Control	16

4.3.1.2 Voltage Control & Current Clamp	16

4.3.1.3 Voltage to Alpha Conversion	16

4.3.1.4 Antiparallel Operation	16

4.3.1.5 Power Supply Control Time Window	17

4.3.2 Current Measurement Selection	17

4.3.3 Load Current Calculation	18

4.3.4 Instantaneous Overcurrent (IO) Checks	18

4.3.5  I2T Checks	18

4.3.6 RMS Current Checks	18

4.3.7 OH/PF1b Force Check	20

4.3.8 CHI Checks	20

4.3.9 Value Checks	20

4.3.10 Shutdown Function	20

4.3.11 Fault Function	21

4.4 Lockouts	21

4.4.1 Circuit Lockouts	21

4.4.2 Bipolarity Lockout	22

4.5 Fault Handling	22

4.5.1 Current Clamp	23

4.5.2 Alarm	23

4.5.3 Circuit Fault	23

4.5.4 System Fault	23

5.0 User Interface	24

5.1 Input Data	24

5.1.1 Control Data Files (CDF)	24

5.1.2 Timing Data Files (TDF)	24

5.1.3 Breakpoint Data Files (BDF)	25

5.2 Monitoring	25

5.3 Output Data	25

5.3.1 Collected Data	25

5.3.2 Fault  Data	25

6.0 Implementation of Modes	25

6.1 Features and Functions vs. Modes	25

6.2 Simulation Sub-Mode	26

6.2.1 PS Behavior	26

6.2.2 Coil Behavior	27

7.0 General Implementation Requirements	28

7.1 Documentation	28

7.2 Structure of PSRTC Code	28

| BDF | Breakpoint Data File |
| --- | --- |

| CAMAC | Computer Aided Measurement And Control |
| --- | --- |

| CCD | Capacitor Charge/Discharge Unit |
| --- | --- |

| CDF | Control Data File |
| --- | --- |

| CHI | Coaxial Helicity Injection |
| --- | --- |

| CLR | Current Limiting Reactor |
| --- | --- |

| DCCT | Direct Current Current Transducer |
| --- | --- |

| EOP | End of Pulse |
| --- | --- |

| FF | Fault Function |
| --- | --- |

| FG | Firing Generator |
| --- | --- |

| HCS | Hardwired Control System |
| --- | --- |

| HIS | Hardwired Interlock System |
| --- | --- |

| I2T | ∫i^2(t)dt |
| --- | --- |

| IO | Instantaneous Overcurrent |
| --- | --- |

| MA | Monitoring Application |
| --- | --- |

| MG | Motor Generator |
| --- | --- |

| NSTX | National Spherical Torus Experiment |
| --- | --- |

| OH | Ohmic Heating |
| --- | --- |

| PCW | Plasma Control Window |
| --- | --- |

| PDA | Power Diode Assembly |
| --- | --- |

| PF | Poloidal Field |
| --- | --- |

| PRTC | Plasma Real Time Controller |
| --- | --- |

| PS | Power Supply Unit |
| --- | --- |

| PSCW | Power Supply Control Window |
| --- | --- |

| PSG | Power Supply Group |
| --- | --- |

| PSRTC | Power Supply Real Time Controller |
| --- | --- |

| PSS | Power Supply Section |
| --- | --- |

| RMS | Root Mean Square |
| --- | --- |

| SDS | Safety Disconnect Switch |
| --- | --- |

| SF | Shutdown Function |
| --- | --- |

| SOP | Start of Pulse |
| --- | --- |

| TDF | Timing Data File |
| --- | --- |

| TF | Toroidal Field |
| --- | --- |

1.0 Introduction

This Software Requirements Specification describes the requirements for the NSTX Power Supply Real Time Controller (PSRTC), as well as related software applications to interact with same and provide for the Operator Interface.

The PSRTC acts on the power supply equipment at D-site (WBS 5) and thereby provides control of the application of voltage to the NSTX coils either in direct response to commands from the NSTX Plasma Real Time Controller (PRTC), or as required to produce a  programmable current through the coils via feedback control.

The PRTC in the context of this specification includes the plasma controller as well as associated fault sensing features which serve to integrate the operation of the entire NSTX plant, including the NBI, RF, Gas Injection, etc.

In addition to controlling the interaction of the power supply equipment with the coils, the PSRTC provides control of the application of voltage and the delivery of current to the Coaxial Helicity Injection (CHI) system on NSTX.

2.0 Entities to be Monitored and Controlled

The D-site power supply equipment subject to monitoring and control by the PSRTC consists of components, which are further arranged into circuits, as described in the following.

2.1 Components

2.1.1 Motor Generator Sets

a. Two motor generator (MG) sets exist at D-site. For inductivly driven experiments involving the use of the Ohmic Heating (OH) coil, one of the two MG sets is required to buffer the NSTX power supply load from the utility grid. For experiments with partial or non-inductive operation (OH usage reduced or eliminated) operation directly from the grid may be undertaken in some cases. Therefore the PSRTC shall accommodate operation via one MG set, as well as operation directly from the grid.

b. Control interfaces are available for the MG sets for speed, drive motor power, and voltage setpoints. However for NSTX none of these need to be controlled by the PSRTC in real time since...

- NSTX consumption of stored energy from the MG will be minimal; therefore the speed setting can be made manually by the MG operator at a low value (e.g. 65Hz) such that windage/friction losses are minimized and sufficient energy is available for the NSTX pulse;

- Drive motor power setting can be made manually by the MG operator since there is no need for automated real time control to reduce windage/friction, etc. per the argument above;

- Voltage setpoint adjustment in real time is not presently envisioned for NSTX.

Control of the speed, power, and voltage setpoints is available at the D-Site MG control board to the MG Operator, and is available through the CAMAC system as well, subject to the MG Operator control of a "Local/Remote" switch at the D-site MG control board.

c. A control toggle is available which can be used to select between a reduced excitation mode and a full excitation mode. To reduce eddy/hysteresis losses, it is desirable to utilize this toggle to select the reduced excitation mode between pulses. This is feasible on NSTX because only one MG set is to be used, and therefore no synchronization issues exist. It is envisioned however that (as a feature introduced during the operations phase of NSTX)  this will be accomplished not via the PSRTC but rather through timing module outputs based on the Start of Pulse (SOP) and End of Pulse (EOP) clock events.

d. Measurements of the MG speed, voltage, active power (P), reactive power (Q), apparent power (S), etc. are available via the CAMAC system. In addition the speed and voltage signals shall be available in real time to the PSRTC and monitored to ensure that  programmable requirements for pulsing are satisfied. Since the level of power which NSTX can take from the MG set is much less than its rating, real time monitoring of P, Q, and S is not required.

e. No monitoring of the utility interface by the PSRTC is required. When operating directly from the grid any checking of MG speed and voltage levels (d. above) shall be disabled.

2.1.2 AC/DC Converters

a. The D-site AC/DC Converters, henceforth referred to as "Power Supplies" (PS), consist of 12-pulse phase controlled thyristor rectifiers. Each PS consists of two 6-pulse "Power Supply Sections" (PSS) which are electrically isolated from each other but subject to the same "Firing Generator" (FG). Each PSS is equipped with a full rated bypass module which can carry the load current when the rectifiers are suppressed.

b. Each PSS is rated to produce a maximum average DC output voltage of 1012.85VDC (≈ 1kV), no load, with 13.8kV AC input voltage applied to the converter transformer primary. Nominal pulse current rating of each PSS is 24kA-6sec/300sec. Maximum current is 30kA. Continuous current rating is 3.25kA.

c. The FG of each PS controls, in effect, the voltage produced by its two PSS by phase controlling the thyristor firing pulses in accordance with a Control Word received as an input from the PSRTC. The Control Word is an 11 bit digital command defined as follows:

Bits 1 through 8: 	Firing angle, a.k.a. "alpha" command, 0 = 0o, 255 = 180o

Bit 9:			"Convert" command,  1= rectifier thyristors gated, a.k.a. "fired",

0 = rectifier thyristors gate blocked, a.k.a. "suppressed"

Bit 10: 		Unused

Bit 11:		"Block Bypass" command, 1 = bypass thyristors gate blocked, 			0 = bypass thyristors gated

d. The FG includes a low pass filter with time constant ≈ 0.5 mS on the alpha command.

e. The FG includes an "inversion limit calculator" which, as a function of input AC voltage and frequency limits the effective alpha such that a preset margin angle is preserved. The margin angle, a.k.a. "gamma", and the effective commutation inductance, are set by potentiometers in the FG.

2.1.3 DC Current Transducers

a. Redundant measurements are made of each coil current. At least one  is made using precision "DC Current Transducers" (DCCTs), a.k.a. "Halmars" (the name of the original manufacturer), of various (e.g. 25kA, 50kA) ratings. These are precision devices, with accuracy better than 0.2% and frequency response up to 10kHz.

b. In some cases  both measurements are made with  Halmars. In other cases, leaf type shunts are used for the second measurement, with Dymec fiber optic transcievers. The accuracy is better than 0.2% at DC, with frequency response limited to < 1kHz (estimated, based on limitation of leaf type shunt).

c. Measurements of the coil currents shall be available to the PSRTC in real time.

2.1.4 Hardwired Control System

a. A Hardwired Control System (HCS) provides interlocking of the D-site power supply equipment for equipment protection and personnel safety purposes. The HCS is supervised by the facility wide Hardwired Interlock System (HIS). The operators of the  HIS control the issuance of permissive signals, resets, etc. to the HCS. The various power supply components are interconnected such that fault information is communicated by the HCS between components and the equipment is de-energized to prevent damage. This system can override commands from the computer generated control software.

b. For NSTX, in the context of the PSRTC, the HCS will be subdivided into  three discrete systems, namely the TF, OH, and the PF/CHI systems. . The two possible fault states for these systems are faulted, and not faulted; there will be no further discrimination into fault levels.

c. The fault status of the HCS shall be monitored by the PSRTC every time step.

2.1.5 Other

During Test Mode (sec. 4.1.1.b) it is desirable to be able to energize the CHI power supply without it being connected to the machine. Therefore to ensure that it is not connected during this mode the PSRTC shall monitor the position of the CHI Safety Disconnect Switch (SDS) line switches.

2.2 Circuits

2.2.1 Circuit Configurations

There are four distinct types of electrical circuit configurations used on NSTX as shown on Figure 2.2.1-1. The boxes which enclose the thyristor symbol represent one or more PSS.

The unlabeled boxes represent groups of one or more coils. The black circles represent nodes, the white circles represent bus link connection points.

Figure 2.2.1-1: NSTX Circuit Configurations

a. Type I is a "Unipolar", "2-Wire" circuit. Current flows in one direction through one load coil group.

b. Type II is a "Unipolar", "3-Wire" circuit. Current flows in one direction through two load coil groups; the magnitude of the current may be different in the two "twin" load coil groups.

c. Type III is a "Bipolar", "2-Wire" circuit. Current flows in either direction through one load coil group.

d. Type IV is a "Bipolar", "3-Wire" circuit. Current flows in either direction through two load coil groups; the magnitude and polarity of the current may be different in the two "twin" load coil groups.

2.2.2 Listing of NSTX Circuits

a. A listing of the NSTX sub-circuits (each coil group comprises a sub-circuit) along with a description of the grouping of twin circuits into the various types, and number of DC poles (cable runs)  is given in Table 2.2.2-1.

Table 2.2.2-1: Circuit Listing

| Sub-circuit | Circuit Type | DC Poles |
| --- | --- | --- |

| TF | I | 2 |
| --- | --- | --- |

| OH | III | 2 |
| --- | --- | --- |

| PF1a Upper | II | 3 |
| --- | --- | --- |

| PF1a Lower |  |  |
| --- | --- | --- |

| PF1b | I | 2 |
| --- | --- | --- |

| PF2 Upper | II | 3 |
| --- | --- | --- |

| PF2 Lower |  |  |
| --- | --- | --- |

| PF3 Upper | IV | 3 |
| --- | --- | --- |

| PF3 Lower |  |  |
| --- | --- | --- |

| PF4 | I | 2 |
| --- | --- | --- |

| CHI | I | 2 |
| --- | --- | --- |

| Spare |  | 2 |
| --- | --- | --- |

| Total | 12 ckt | 21 pole |
| --- | --- | --- |

b. The voltage applied to, or the current produced in, each of the coil groups must be explicitly controlled. Therefore, eleven (11) separate sub-circuit control loops will be required in case all of the bus links depicted in Figure 2.2.1-1 are in place, plus one spare, for a total of twelve (12). However, it is noted that if the bus links are not installed in the Type II and Type IV circuits, then they reduce to Type I and Type III, respectively, and the number of explicit control loops is correspondingly reduced.

c. When the bus links are not in place two halves of the former Type II or Type IV circuits shall be treated in all respects by the PSRTC as single Type I or Type III circuits, respectively.

d. When the bus links are in place the current through the link branch shall be explicitly determined and monitored by the PSRTC every time step.

2.2.3 Utilization of PS in the Circuits

a. A listing of the Power Supply Groups (PSG) installed in each sub-circuit, along with their make up,  is given in Table 2.2.3-1.

Table 2.2.3-1: Power Supply Utilization

| PS Group | Series PSS | Parallel PSS Branch | Tot | D-site (TFTR) ID's of PS |
| --- | --- | --- | --- | --- |

| OH (+) | 6 | 1 | 6 | ETF2-PSS-1A,3A,5B,7B,9B, EEF2-PSS-1B |
| --- | --- | --- | --- | --- |

| OH (-) | 6 | 1 | 6 | ETF2-PSS-2A,4A,6B,8B,AB, EEF2-PSS-2B |
| --- | --- | --- | --- | --- |

| PF1a Upper | 2 | 1 | 2 | EEF4-PSS-2A,2B |
| --- | --- | --- | --- | --- |

| PF1a Lower | 2 | 1 | 2 | EEF3-PSS-1A,1B,2A,2B |
| --- | --- | --- | --- | --- |

| PF1b | 2 | 1 | 2 | EEF4-PSS-1A,1B |
| --- | --- | --- | --- | --- |

| PF2 Upper | 2 | 1 | 2 | EOH5-PSS-1A,1B |
| --- | --- | --- | --- | --- |

| PF2 Lower | 2 | 1 | 2 | EOH3-PSS-1A,1B |
| --- | --- | --- | --- | --- |

| PF3 Upper (+) | 2 | 1 | 2 | EOH2-PSS-1A,1B |
| --- | --- | --- | --- | --- |

| PF3 Upper (-) | 2 | 1 | 2 | EEF1-PSS-1A,1B |
| --- | --- | --- | --- | --- |

| PF3 Lower (+) | 2 | 1 | 2 | EOH4-PSS-1A,1B |
| --- | --- | --- | --- | --- |

| PF3 Lower (-) | 2 | 1 | 2 | EEF1-PSS-2A,2B |
| --- | --- | --- | --- | --- |

| PF4 | 2 | 1 | 2 | EOH6-PSS-1A,1B |
| --- | --- | --- | --- | --- |

| CHI | 2 | 2 | 4 | EOH1-PSS-1A,1B,2A,2B |
| --- | --- | --- | --- | --- |

| TF | 1 | 4 | 4 | ETF1-PSS-1A,1B, 2A,2B,3A,3B,4A, 4B |
| --- | --- | --- | --- | --- |

| Spare | 2 | 1 | 2 |  |
| --- | --- | --- | --- | --- |

| Totals |  | 19 Branch | 21PS/ 42 PSS |  |
| --- | --- | --- | --- | --- |

b. It is noted that there is a total of 15 PSG to be explicitly controlled (including the spare). There is a total of 21 PS units which will comprise those 15 groups at any time. Those 21 PSG may be drawn from any of the units whose D-site (TFTR) ID's are listed. Detailed list of PSS assignments, control addresses, along with DCCT assignments, is given in Appendix I.

2.2.3 Utilization of DCCT in the Circuits

a. DCCT measurements are made, generally,  in each branch of the power supply system which contains PSS. Per Table 2.2.3.1 the total number of PSS branches is 18.

b.  Redundant measurements are made for each coil circuit. Therefore the total number of DCCT measurements which shall be available to the PSRTC is 38. Refer to Appendix I for a detailed listing of assignments.

c. In those cases where there are parallel PSS branches the total current in the coil groups (a.k.a. the "load current") is the sum of the PSS branch currents.

2.3 Summary of Input/Output Requirements

Inputs to the PSRTC from the D-site power supply equipment, and outputs from PSRTC to the equipment, are summarized in Table 2.3.1-1. Refer to Appendix I for details.

Table 2.3.1-1: Summary of PSRTC I/O Requirements

| Description | Type | Quantity | Comments |
| --- | --- | --- | --- |

| DCCT measurements* | Analog** Input | 38 | 2 per PSS branch |
| --- | --- | --- | --- |

| MG Speed | Analog** Input | 1 |  |
| --- | --- | --- | --- |

| MG Voltage | Analog** Input | 1 |  |
| --- | --- | --- | --- |

| HCS Fault Status | Digital Input | 3 bits | 1 TF, 1 OH, 1 PF/CHI |
| --- | --- | --- | --- |

| CHI SDS Line Switch State | Digital Input | 2 bits | 1 for open, 1 for closed |
| --- | --- | --- | --- |

| PS Control Word | Digital Output | 15 words (11 bit) | 1 per PSG |
| --- | --- | --- | --- |

*Ultimate requirement, including spares and future DCCT installations

** Digitized version of continuously variable analog signal

3.0 Interface with Plasma Real Time Controller (PRTC)

3.1 Plasma Control Time Window

A programmable time window (i.e. an interval of time which is adjustable via settings entered by the operator), hereafter referred to as the Plasma Control Window (PCW), shall be established during which interaction will occur between the PSRTC and the PRTC. This interaction includes the communication of reference signals, commands, and fault information, and shall encompass that period during which the plasma current is expected to be present.

3.2 Reference Signals Provided in Real Time by the PRTC

The PRTC shall provide, during the PCW, commands to the PSRTC for the voltage to be applied to the eleven (11) OH, PF, CHI, and Spare circuits listed in Table 2.2.1.

3.3 PRTC/PSRTC Interface

3.3.1 PRTC to PSRTC Signals

a. PRTC shall provide, during the PCW, an overall status signal, indicating that it is available and functional, and that no other faults (e.g. "discharge faults" or others as deemed appropriate by the PRTC design) exist. If and when this signal reverts to the "Not Ready" state during the PCW the PSRTC shall transition to the Fault State (sec. 4.1.3.e). The PSRTC shall latch this signal, i.e. if it first transitions from "Ready" to "Not Ready", and then transitions in the opposite sense, the second transition will be ignored by the PSRTC.

b. PRTC shall provide, during the PCW,  voltage references for the eleven (11) (i.e. 10 + 1 Spare) PF, OH, and CHI circuits.

c. PRTC shall provide, during the PCW, a status signal when plasma control is "Active". When plasma control is completed the signal shall transition to the "Inactive" state. The PSRTC shall latch this signal, and transition to the Shutdown Phase (sec. 4.1.4).

3.3.2 PSRTC to PRTC Signals

a. PSRTC shall provide an overall status signal, indicating that it is available and functional The PSRTC shall latch this signal into the fault state on first occurrence of any fault in this category.

b. PSRTC shall provide individual lockout status signals for each of twelve (12) TF, OH, PF, CHI, and Spare circuits listed in Table 2.2.1. The two states shall be "Active" and "Locked Out" for each. Note: these signals do not change in real time.

c. The PSRTC shall provide individual current clamp status signals for each of the twelve (12) TF, OH, PF, CHI, and Spare circuits listed in Table 2.2.1, indicating whether or not the magnitude of the coil current is within limits (not being clamped by the PSRTC). The two states shall be "OK" and "Limit" for each. The PSRTC shall not latch this signal.

d. The PSRTC shall provide individual fault status signals for each of the twelve (12) TF, OH, PF, CHI, and Spare circuits listed in Table 2.2.1, indicating whether or not a software fault has been detected in each system. The two states shall be "OK" and "Limit" for each.The PSRTC shall latch each signal on first occurrence of a fault in the circuit which it represents.

4.0 Control Features

4.1 Modes, Sub-Modes, States, and Phases of Operation

The PSRTC shall provide for the following modes, sub-modes, and states, of operation.

4.1.1 Modes

The three mutually exclusive modes shall be Normal, Test, and Dummy Load.

a. Normal Mode is defined as that during which the PSRTC is controlling the application of the output of the power supplies on to the NSTX machine coils and CHI electrodes, and interaction with the PRTC is enabled.

b. Test Mode is defined as that during which the PSRTC is operating as it would in the Normal Mode except that the interaction with the PRTC is disabled, and CHI operation is disabled by ensuring that the line switches in the CHI Safety Disconnect Switch (SDS) cabinet are open.

c. Dummy Load Mode is defined as that during which the PSRTC is controlling the application of the output of one of the power supply circuits on to a dummy load, and interaction with the PRTC is disabled.

4.1.2 Sub-Modes

The two mutually exclusive sub-modes shall be Operation and Simulation.

a. Operation Sub-Mode is defined as that during which the commands from, and input data to, the PSRTC, are based on interaction with the actual power supply system hardware.

b. Simulation Sub-Mode is defined as that during which the PSRTC is functioning as it would in the Operation Sub-Mode except that the response of the power supply system, coils, and CHI, as well as the input from the PRTC, are simulated.

4.1.3 States

The three mutually exclusive states shall be Pulse State, Standby State, and Fault State.

a. Pulse State shall be defined as that during which the power supplies are energized and current flows in the coils.

b. Standby State shall be defined as that during which the power supplies are de-energized and current does not flow in the coils.

c. Transition from the Standby State to the Pulse State shall be initiated after an appropriate delay following the receipt of a trigger signal from the NSTX Facility Clock System corresponding to Start of Pulse (SOP). The delay shall correspond to the interval between the SOP event and the earliest event associated with the operation of the power supplies, including capacitor bank charging.

d. Transition from the Pulse State to the Standby State shall be completed prior to expiration of the time allocated for the Pulse State, during which all operations necessary to  drive  and extinguish currents in coils shall be completed.

e. Fault State shall be defined as that during which all PSS are suppressed and bypassed The Fault State can be entered from either the Standby State or the Pulse State, due to the occurrence of various events to be described. To exit from the Fault State requires a Reset command from the Engineering Operator.

4.1.4 Phases

For the Normal Mode of operation (PRTC interaction enabled) only, the three mutually exclusive phases during the Pulse State shall be Initialization, Plasma, and Shutdown.

a. The Initialization Phase shall commence at the start of the Pulse State, and shall be utilized to establish the initial currents and fields prior to enabling the PRTC.

b. The Plasma Phase shall commence after a  programmable delay following SOP. During this phase the interaction with the PRTC shall be enabled (the Plasma Control Window (PCW)).

c. The Shutdown Phase shall commence after a  programmable delay following SOP, or when requested earlier by the PRTC. During this phase the interaction with the PRTC shall be disabled, and the Shutdown Function (sec. 4.3.11) shall be requested.

4.2 Timing

a. Timing resolution for the PSRTC shall be 1.0 millisecond. Calculations shall be repeated once per millisecond. Under no circumstances shall calculations be skipped. Tolerance on 1mS interval shall be approximately +/- 10 µS.

b. Input data shall be sampled approximately 200 microseconds or less prior to its use in the calculations.

c. Calculation cycle shall be completed within approximately 600 microseconds or less (worst case).

d. Commands generated by the calculations shall be received by the components within approximately 200 microseconds or less following the completion of the calculation cycle.

e. Specification of time dependent information (reference waveform data, misc. event initiation, etc.) shall be input by the Engineering Operator in time relative to "T0", the nominal time at which plasma operations begins during a pulse (time of beginning of plasma initiation process). The overall timing reference shall be the SOP signal generated by the NSTX Facility Clock System. The time delay between SOP and T0 (∆TSOP) shall be  programmable.

f. The Pulse State shall encompass the interval between earliest and latest of all time dependent events specified to the PSRTC  An error shall be declared in case the Pulse State exceeds the window set by SOP and EOP (where EOP is determined by the setting of the NSTX Facility Clock System). Maximum duration of pulse state shall be 10 seconds.

4.3 Functions

4.3.1 Power Supply Control Function

The Power Supply Control Function is depicted in Figure 4.3.1. The same basic function is applied to all of the circuits.  The output of the control function consists of the firing angle (α) and convert bit commands which are delivered to the PS in the form of the PS Control Words. Since the firing angle is related to the voltage, these commands are, essentially, voltage commands. The voltage commands are derived either from closed loop proportional - integral (PI) current control against a  programmable reference, or from a direct voltage request. The direct voltage request is obtained from either a  programmable reference, or a signal supplied in real time by the PRTC. When in the voltage control mode, a current clamp feature is applied if the current approaches a  programmable limit. Additional features include rate limiting, and control of antiparallel rectifiers, including the required α limiting. Following is a description of these features, with reference to Figure 4.3.1.

4.3.1.1 Closed Loop Current Control

The load current Iload is subtracted from a  programmable reference Ireference. The difference is the error Ierror. Ierror is multiplied by proportional gain Gp, and is integrated and multiplied by integral gain Gi. The sum of these two terms is the voltage requested by current control Vcurrent. The integrator includes an "anti-wind-up" reset feature which is a function of time; one reset time shall be allowed per circuit.

4.3.1.2 Voltage Control & Current Clamp

The source of the command Vcommand can be either the  programmable reference Vreference or a real time signal provided by the PRTC VPRTC. The time window during which VPRTC is enabled shall correspond to the PCW. Voltage control is subject to an override by a current clamping feature which comes into play when limits are reached. The clamping is based on PI control which generates a voltage adjustment term Vclamp whenever the load current Iload passes outside the range between the positive and negative clamp settings Iclamp>0 and Iclamp<0. When the current returns to the allowable range the clamp integrator is reset. The net voltage request based on voltage control Vvoltage is the result of the addition of Vcommand and Vclamp.

4.3.1.3 Voltage to Alpha Conversion

The selection of the source of the voltage request V0 from either voltage control Vvoltage or current control Vcurrent is a function of time. V1 is the per unit version of V0 based on V1=V0/Vmax, where Vmax is the maximum no-load voltage available for the circuit in question. Vmax is based on the  programmable number of series PSS (NS), and the primary side AC rms line-to-line source voltage E (nominally 13.8kV at D-site). V2 is a rate and magnitude limited version of V1, where the rate limit is  programmable for each circuit and the magnitude limit is -1 to 1 per unit. The rate limit is only applied when the antiparallel mode is in effect (see 4.3.1.4). α0 is the firing angle request, and α1 is the final firing angle command after limiting. If antiparallel operation is not in effect, then the allowable range of α1 is 0 to αmax , where αmax is the maximum permissible delay angle. It is calculated based on the load current per PSS, equal to Iload/NP where NP is the number of parallel PSS branches in the circuit being controlled,  the AC source frequency ω, the commutating inductance Lc, and the AC source voltage E, along with a  programmable inversion margin angle γ. If antiparallel operation is in effect, then the minimum permissible delay angle αmin is set equal to 180 - αmax , so that the allowable range of alpha is therefore αmin ≤ α1 ≤ αmax in the antiparallel mode.

4.3.1.4 Antiparallel Operation

a. Antiparallel Operation permits bipolar current flow in the load without delay around current zero. When it is in effect, the antiparallel converters (a.k.a. the (+) and (-) converters) must be operated at symmetric (about 90 degrees) delay angles αmin and αmax. This is required to minimize the circulating current which is impeded only by the Current Limiting Reactors (CLRs). The antiparallel mode is declared when the magnitude of the load current Iload falls below a threshold Ithresh. Thus the comparison is conditioned by a

hysteresis function which only declares the mode to be true if the previous magnitude exceeded the threshold.

b. A switch shall provided to enable/disable antiparallel operation.

4.3.1.5 Power Supply Control Time Window

a. For each circuit a PS control window (PSCW) shall be established based on the start and end time of the reference waveform for that circuit. Inside the PSCW the PS control function shall be executed. Outside the PSCW the PS Control Word shall be set to suppress, bypass, and fully invert the PS in that circuit:

Bits 1 through 8: 	Firing angle = 180o

Bit 9:			"Convert" command = 0

Bit 10: 		Unused

Bit 11:		"Block Bypass" = 0

4.3.2 Current Measurement Selection

a. Two redundant measurements are generally available for each PSS branch current. At each time step, the difference between the magnitude of the two measurements shall be calculated and compared to a  programmable allowable as a check for the validity of the measurements as follows:

∆Ij = |I1j|-|I2j|

Discrepancy condition declared if:

∆Ij > ∆Imaxj

Where:

j		= 1 to number of parallel PSS branches

I1j		= first measurement of current for branch "j"

I2j		= second measurement of current for branch "j"

∆Ij		= difference

∆Imaxj 	= allowable difference

b. The measurement with the larger magnitude shall be selected for further processing:

Ij = Pmax*max(|I1j|,|I2j|)

Pmax		= polarity of measurement with larger magnitude

Ij		= larger of two branch "j" current measurements

4.3.3 Load Current Calculation

Each circuit has specific requirements for summing the measurements from the individual PSS branches to determine the total current, in terms of polarity interpretation and number of branches to be summed. Therefore for each circuit the following summation shall be performed:

Iloadi = Plinki*∑ Pbranchij*Imaxij

Where:

i 		= circuit "i" (1 to 12)

Iloadi 		= total load current for circuit "i"

Plinki		= bus link polarity for circuit "i"

j		= 1 to number of parallel PSS branches (NPi) in circuit "i"

Imaxij		= larger of two circuit "i" branch "j" current measurements

Pbranchij	= polarity interpretation for branch current measurement "j" in circuit "i"

4.3.4 Instantaneous Overcurrent (IO) Checks

a. Each time step the magnitude of the current in each PSS branch Imaxij and the magnitude of the total load current Iloadi  in each circuit, shall checked against  programmable limits.  For each circuit there shall be two sets of limits, one effective during the PSCW and one outside the PSCW.

4.3.5  I2T Checks

During each pulse, for each circuit, within the PSCW, the ∫i2(t)dt (I2T) shall be computed based on the total load current Iloadi  , and shall checked against a  programmable limit. At the start of a new pulse the integral shall be reset.

4.3.6 RMS Current Checks

a. A simulation of the temperature of the cables which comprise the 21 DC poles (the connections to the load coil groups, Table 2.2.2.1) shall be performed, in effect ensuring that the RMS current flow in the cables is within limits. The current in each pole is equal to either a) one of the load currents, or b) a sum of a pair the load currents:

Ipolek = ∑ Ppolekl*Iloadkl

Where:

k		= DC pole "k" (1 to 21)

Ipolek 		= current for pole "k"

l		= 1 to number of load current for pole "k"

Iloadkl		= pole "k" load current "l"

Ppolekl	= polarity interpretation for pole "k" load current "l"

Simulation shall be performed for each pole using the following algorithm executed each time step:

Rpole = Rpole20*(1+coeff*(Tpole-20))

∆Tpole = ∆Tpole + (Ipole2*Rpole-∆Tpole/TRpole)*dt/TCpole

Tpole = T0 + ∆Tpole

Where:

Tpole		= cable temperature (oC)

T0		=  programmable ambient temperature (oC)

∆Tpole		= temperature rise (oC)

Ipole		= current in pole

Rpole20	= ohmic resistance of pole cables at 20oC

TRpole	= thermal resistance of pole cables

TCpole	= thermal capacity of pole cables

coeff		= copper thermal coefficient of resistance = 0.0041 per oC

This simulation is based on an electrical analog of the thermal behavior of the cables, based on a single thermal time constant model per the equivalent circuit given in Figure 4.3.7-1.

Figure 4.3.7.1 - Single Time Constant Thermal Model

b. Simulated temperature of each pole shall be compared to an allowable. Alarm shall be generated if temperature exceeds the allowable.

c. When the PSRTC is restarted, the initial cable temperatures shall be set to values contained in an input file, nominally equal to the ambient temperature T0. If the PSRTC needs to be restarted during an NSTX operational day during which prior cable heating may have occurred, not known to the restarted simulation, the Engineering Operator will be thus be able to initialize to values estimated to reflect actual conditions.

d. The RMS Current Check shall be performed continuously once the PSRTC is restarted. However, it shall assume that the currents are exactly zero (0) during the Standby State and Fault State, and take the currents into account only during the Pulse State, and only when in the Operation Sub-mode (when in the Simulation Sub-mode, the simulated currents shall be ignored).

4.3.7 OH/PF1b Force Check

The ability of the NSTX machine to withstand repulsive forces (a.k.a. "launching loads") between the OH and PF1b coils is limited. Therefore the product of Ioh and IPF1b shall be limited to a  programmable allowable. Since repulsion occurs whenever the two currents are in the opposite direction, the product will always be negative in the quadrants of concern. Therefore the constraint shall be that Ioh * IPF1b ≥ a  programmable allowable called Alaunch.

4.3.8 CHI Checks

a. CHI requires the presence of a Toroidal Field in order to function properly. Therefore if |Ichi| > programmable value Ichi0 then |Itf| shall be always be ≥  programmable value Itfmin. If not, the CHI circuit shall be considered faulted.

b. If the TF circuit is faulted, then the CHI circuit shall be considered faulted as well.

c. In addition to the real time check called out in a. above, the preprogrammed waveforms shall be checked to ensure that the PSCW for CHI falls within the time window during which the preprogrammed |Itf| is ≥ programmable value Itfmin.

d. CHI requires that the relative polarity of the injected current and the Toroidal Field must be correct (both positive (TF clockwise (CW) viewed from above, and Ichi flowing into center stack (CS) casing) or both negative (TF CCW and Ichi flowing out of CS casing)). However, it is not required that the PSRTC check for this in real time. Instead, the polarity of the bus links (programmable input data, see sec. 4.3.3, 5.1.1) shall be both (TF and CHI) positive, or both negative.

4.3.9 Value Checks

a. Value checks are defined as checks of values of specified variables at specified times against  programmable values. PSRTC shall support up to ten (10) value checks, none of which shall occur at the same time.

b. For each value check, the variable name, check time, target value, relationship (=, ≠, < , ≤, >, ≥), and response (alarm, fault level) shall be programmable, in accordance with the logic If-Variable-Value-Relationship-Then-Response. The pre-defined menu of variables whose values can be checked shall consist of those listed in Appendix IV.

4.3.10 Shutdown Function

a. The shutdown function (SF) is provided to allow for the simultaneous controlled shutdown of the currents in all circuits, using a simple and reliable action, based on a constant firing angle (approximately constant voltage, constant current derivative) scenario.

b. The shutdown function shall be invoked based on command from the PRTC (sec. 4.1.4.c) and/or at a  programmable time relative to SOP.

c. The shutdown current derivative (SCD) shall be programmable for each circuit. The shutdown voltage Vsd shall be precalculated based on the self inductance L of the circuit in question according to:

Vsd = L*SCD

The shutdown firing angle αsd shall be precalculated according to:

αsd = COS-1(Vsd/Vmax)

Where Vmax is precalculated according to:

Vmax = NS*3*sqrt(2)*E*0.75/π/13.8

Where NS is the number of series PSS in the circuit, and E is the  programmable AC rms line-line voltage at the converter primary (nominally 13.8kV) level.

d. To prevent errors due to bad input data, a constraint shall be imposed such that αsd ≥ 90 degrees.

e. When the SF is requested, the following actions shall take place:

• PS control function shall be suspended;

• PS Control Words shall be issued to the PS in each circuit according to the following logic:

- if Iload ≥ 0, command to convert @ αsd  issued to all (+) polarity PS, command to suppress issued to all (-) polarity PS, all bypass are blocked

- if Iload < 0, command to convert @ αsd  issued to all (-) polarity PS, command to suppress issued to all (+) polarity PS, all bypass are blocked

4.3.11 Fault Function

a. The fault function (FF) is provided to allow for the  de-energization and bypassing of  individual circuits using a simple and reliable action. When the FF is requested, the following actions shall take place:

• PS control function shall be suspended, and PS Control Words shall be issued all PS in the faulted circuit to suppress, and bypass;

• Fault status of faulted circuit shall be latched;

• If Normal Mode, Fault status of faulted circuit shall be communicated to PRTC (sec. 3.3.2.d)

b. Twin circuits (Type II and Type IV "three wire" configurations (Figure 2.2.1-1)) shall be treated together in the context of fault response and fault reporting. When one of the two circuits which comprise a pair of these Types is faulted, then the twin circuit shall also be considered faulted and shall be treated accordingly. The twin circuits are PF1a Upper and Lower, PF2 Upper and Lower, and PF3 Upper and Lower.

4.4 Lockouts

4.4.1 Circuit Lockouts

a. In Normal and Test Modes, a feature shall be provided to permit the lockout of any one or more of the 12 circuits. When a circuit is locked out, all functions related to that circuit shall be skipped/disabled. In Dummy Load Mode, only one circuit shall be active; all others shall, by definition, be locked out.

b. Control Word commands shall be issued to the PS in circuits which are locked out, calling for gate suppression of both the bypass and power module gates (mode bits 11, 10, and 9 equal to 1,0,0, respectivly).

c. Special Lockout treatment is required for circuits which can be arranged into the Type II and Type IV "three wire" configurations (Figure 2.2.1-1). When one of the two circuits which comprise a pair of these Types is locked out, then control of that circuit, and related functions, shall revert to its twin circuit. The twin circuits are PF1a Upper and Lower, PF2 Upper and Lower, and PF3 Upper and Lower. When either of the twin circuits is locked out:

• The same Control Word shall be delivered to all of the PS which comprise the two twin circuits, based on the control function calculations driven by reference data supplied to the active one of the two circuits;

• The load current OC (sec. 4.3.4) , and I2T check (sec. 4.3.5) for the locked out circuits shall be skipped;

• The load current calculation (sec. 4.3.3), and the RMS check (4.3.6) shall still be executed, in case the bus links in the third wire are still in place, even though one of the twins is locked out (this is still a valid mode of operation; under ideal conditions the current through the third wire will be zero).

4.4.2 Bipolarity Lockout

A feature shall be provided to lock out all aspects of antiparallel control in the PS control function. It shall be the responsibility of the Engineering Operator to ensure that this lockout selection is in conformance with the configuration of the hardware (e.g. bus links and SDS switches).

4.5 Fault Handling

Four levels of faults shall exist as indicated in Table 4.5-1. A subset of the faults shall be communicated to the PRTC. All fault events shall be recorded in a FIFO memory area capable of storing fault description, effected circuit, time of occurrence, and fault variable value for 100 fault events.

Table 4.5-1: Fault Levels

| Description | Report to PRTC | PSRTC Response |
| --- | --- | --- |

| Current Clamp | x |  |
| --- | --- | --- |

| Alarm |  |  |
| --- | --- | --- |

| Circuit Fault | x | Fault Function* |
| --- | --- | --- |

| System Fault | x | Fault Function, all circuits |
| --- | --- | --- |

*See sec. 4.3.11

4.5.1 Current Clamp

Current Clamp shall be declared on a per circuit basis whenever the PS control function current clamping is in effect; it is not a latched fault state.

4.5.2 Alarm

Alarm shall be declared on a per circuit basis whenever alarm level faults occur; it is not a latched fault state. Circuit Alarm faults consist of the following:

• DCCT Discrepancy (disagreement between DCCT measurements, sec. 4.3.2.a)

-This condition indicates a transducer problem but does not warrant immediate shutdown.

•

• RMS Overcurrent (sec. 4.3.6)

- This condition indicates a violation of the load current envelope in terms of pulse current and/or repetition rate, and/or misoperation of twin PS in the Type II or Type IV circuits. Since the cable thermal time constants are quite long, and the cable temperature rise per pulse is small compared to the allowable temperature rise over time, this condition does not warrant immediate shutdown.

• Value Check Faults per preprogramming (sec. 4.3.9)

4.5.3 Circuit Fault

Fault shall be declared on a per circuit basis (except for the twin Type II or Type IV circuits, see sec. 4.3.11.b) whenever a fault in this category occurs; it shall lead to the latched Fault State (sec. 4.1.3.e). However, following the occurrence of the first fault, any subsequent fault events shall still be recorded. Faults consist of the following:

• Receipt of fault indication from HCS (note that the PF/CHI circuits are grouped together in this regard)

• Instantaneous Overcurrent Faults (sec. 4.3.4, due to branch or load overcurrents)

• I2T Fault (sec. 4.3.3.a)

• CHI  Faults (sec. 4.3.8, lack of Btf with |Ichi| > 0.)

• Launching Load Fault (sec. 4.3.7, product of Ioh and IPF1b exceeds allowable)

• Value Check Faults per preprogramming (sec. 4.3.9)

4.5.4 System Fault

Internal self-test features shall be included in the PSRTC software to detect failure of the hardware/software, data links, etc.. In case of such failures the system shall latch to the fault state and all circuits shall enter the Fault Function.

5.0 User Interface

User Interface shall provide for:

• Control of PSRTC Mode;

•  Creation and loading* of input control, timing, and breakpoint data files;

• Display of various CAMAC devices related to operation of the PSRTC;

• Retrieval* and display of selected PSRTC variables;

• Retrieval*, display, and storage of selected PSRTC control variable waveforms collected during the prior pulse;

• Retrieval*, display, and storage of fault data collected during the prior pulse.

*Note: interaction with PSRTC during Standby State only

5.1 Input Data

5.1.1 Control Data Files (CDF)

a. List of Control Data is given in Appendix II, along with default values, allowable range, and preprocessing requirements.

b. Mechanism for creation, storage, and retrieval of multiple CDF shall be provided.

c. "Save As" feature shall be provided such that  new copy of existing files can be created with a new name.

5.1.2 Timing Data Files (TDF)

a. TDF contain event time data and description of timing windows. In addition they contain links to Breakpoint Data Files (BDF) and CDF such that:

• Multiple TDF may be associated with a single CDF;

• Multiple TDF may be associated with a single BDF.

b. List of Timing Data is given in Appendix III, along with default values and preprocessing requirements.

c. Mechanism for creation, storage, and retrieval of multiple TDF shall be provided.

d. "Save As" feature shall be provided such that  new copy of existing files can be created with a new name.

e. Mechanism for superimposed display of complete waveform set (12 waveforms, one per circuit) shall be provided.

5.1.3 Breakpoint Data Files (BDF)

a. BDF contain waveform data in the form of breakpoints.

b. The form of the data consists of (time, value, interpretation), where interpretation is voltage or current, up to 100 breakpoints per file.

c. Mechanism for creation, storage, and retrieval of multiple BDF shall be provided.

d. "Save As" feature shall be provided such that  new copy of existing files can be created with a new name.

e. Mechanism for display of complete waveform shall be provided.

5.2 Monitoring

a. A Monitoring Application (MA) based on a Graphical User Interface (GUI) with multiple windows shall be created to facilitate operation of the PSRTC.

b. The State of the PSRTC shall be displayed, along with selected CAMAC based signals listed in Appendix V.

c. The MA shall permit the Engineering Operator to navigate between windows for the control of the State, the monitoring, the display of collected data, the entry of control and timing data, etc.

5.3 Output Data

5.3.1 Collected Data

The PSRTC, as well as the MA, shall provide for the collection and display of up to 48 of the variables listed in Appendix IV. The MA shall provide for the editing of the collected data request list by the Engineering Operator prior to each pulse. The data for each of the selected variables shall be collected for each millisecond for the entire duration of the Pulse State.

5.3.2 Fault  Data

The PSRTC, as well as the MA, shall provide for the collection and display of the FIFO containing the fault event record (sec. 4.5).

6.0 Implementation of Modes

6.1 Features and Functions vs. Modes

Table 6.1-1 indicates the features and functions which shall be active in the various modes.

Table 6.1-1: Functions & Features vs. Mode

| Function/Feature | Normal | Test | Dummy Load |
| --- | --- | --- | --- |

| PRTC Interface | x |  |  |
| --- | --- | --- | --- |

| PS Control | x | x | One circuit at a time |
| --- | --- | --- | --- |

| Current Measurement Selection | x | x | x |
| --- | --- | --- | --- |

| Load Current Calculation | x | x | x |
| --- | --- | --- | --- |

| Overcurrent Checks | x | x | x |
| --- | --- | --- | --- |

| I2T Checks | x | x | x |
| --- | --- | --- | --- |

| RMS Checks* | x | x | x |
| --- | --- | --- | --- |

| OH/PF1b Force Checks | x | x |  |
| --- | --- | --- | --- |

| CHI Checks | x |  |  |
| --- | --- | --- | --- |

| Value Checks | x | x | x |
| --- | --- | --- | --- |

| Shutdown Function | x | x | x |
| --- | --- | --- | --- |

| Fault Function | x | x | x |
| --- | --- | --- | --- |

| Lockouts | x | x | x |
| --- | --- | --- | --- |

| Fault Handling | x | x | x |
| --- | --- | --- | --- |

*Account for currents during Pulse State, in Operation Sub-Mode (not Simulation) only

6.2 Simulation Sub-Mode

6.2.1 PS Behavior

a. For each circuit the power supplies shall be modeled using the equivalent circuit shown in Figure 6.2.1-1.

Figure 6.2.1-1: PS Equivalent Circuit

Vdo = NS*3*sqrt(2)*E*0.75/π/13.8

R = NS*6*f*Lc

Id = Iload/NP

Vd = Vdo*COS(α) - Id * R

Where:

Vdo 	= maximum available no load average DC voltage

Vd 	= regulated average DC voltage

Id	= effective DC current per PSS

E	= AC source voltage (line-line kV rms at the 13.8kV level)

f 	= AC source frequency

R	= effective resistance due to commutation voltage drop

NS 	= number of series PSS

Lc	= commutating inductance

NP 	= number of parallel PSS

b. For each circuit, if the bipolar mode is active (not locked out), current flow shall be permitted in both directions. Otherwise, it shall be unidirectional.

c. Increases in the firing angle α shall be rate limited according to dα/dt ≤ 360*f degrees/second. Decreases shall not be rate limited.

d. The active (P) and reactive (Q) power demand of each circuit "i" shall be calculated according to:

Pi = Vd*Id

Qi = sqrt((Vdo*Id)2-Pi2)

e. The net power demand, including the apparent power (S) shall be calculated according to:

Pnet = ∑Pi

Qnet = ∑Qi

Snet = sqrt(Pnet2+Qnet2)

6.2.2 Coil Behavior

a. Coils shall be simulated with due consideration of the temperature rise and change of ohmic resistance, as well as the self and mutual inductance between PF and OH coils. No mutual coupling shall be included between the TF and CHI circuits and other circuits.

b. Effects of eddy currents in passive structure need not be simulated.

c. Simulation shall solve the matrix equation...

[V] = [M]*[dI/dt]+[R]k*[I]

The method used shall solve for the current derivatives and apply an Euler integration each iteration step "k"....

[X] = [M]-1

[Y]k+1 = [V]k-[R]k*[I]k

[dI/dt]k+1 = [X]*[Y]k+1

[I]k+1 = [I]k + [dI/dt]k+1 * ∆t

d. Coil resistance shall be updated at each time step according to...

[W]k+1 = [W]k + [I]2k* [R]k*∆t

[∆T]k+1 = [W]k+1 / [TC]

[R]k+1 = [R20] * (1+ coeff*(Tinlet+[∆T]k+1 - 20))

Where:

W		= energy dissipation

∆T		= temperature rise (oC)

T0		=  programmable cooling water inlet temperature (oC)

R20		= ohmic resistance of coils at 20oC

TC		= thermal capacity of coils

coeff		= copper thermal coefficient of resistance = 0.0041 per oC

e. Circuits which are locked out shall be assumed open circuited in the simulation.

f. Special Lockout treatment is required for circuits which can be arranged into the Type II and Type IV "three wire" configurations (Figure 2.2.1-1). When one of the two circuits which comprise a pair of these Types is locked out, the simulation channel of that circuit shall be joined with its twin circuit, such that the electrical resistance is doubled, the thermal capacity is doubled,  and the inductance is set equal to 2*(Lii + Lij). The twin circuits are PF1a Upper and Lower, PF2 Upper and Lower, and PF3 Upper and Lower.

7.0 General Implementation Requirements

7.1 Documentation

Separate Software Design Descriptions shall be written to document the PSRTC and the User Interface applications.

7.2 Structure of PSRTC Code

PSRTC code shall be subdivided into platform related categories, namely:

• code which is computer hardware specific

• code which is independent of the hardware

The code shall be structured in such a way that the hardware specific parts can be readily isolated from the hardware independent parts.

APPENDIX I

List of Input/Output Signals

APPENDIX II

List of Control Input Data

APPENDIX III

List of Timing Data

APPENDIX IV

List of Variables for Value Check Function

&

Collection During Pulse

APPENDIX V

List of CAMAC Devices

for

Display by

Monitoring Application