National Spherical Torus Experiment

NSTX

SPECIFICATION

FOR

SURGE SUPPRESSOR ASSEMBLIES

NSTX-SPEC-5X-051

Revision 0

July 14, 1998

PREPARED BY:_____________________________

S. Ramakrishnan

REVIEWED BY:_____________________________

F. Malinowski

APPROVED BY:_____________________________

C. Neumeyer

PRINCETON UNIVERSITY

PLASMA PHYSICS LABORATORY

(PPPL)

P.O. BOX 451

PRINCETON, N.J. 08543

609-243-2000

| Revision | Date | TRB | Description of Change |
| --- | --- | --- | --- |

| First Issue | July 14, 1998 |  |  |
| --- | --- | --- | --- |

1.0 SCOPE	1

2.0 APPLICABLE DOCUMENTS	1

3.0 REQUIREMENTS	1

3.1 PERFORMANCE REQUIREMENTS	1

3.1.1 PERFORMANCE CHARACTERISTICS	1

3.1.2 ENVIRONMENTAL	1

3.1.3 DESIGN LIFE	1

3.1.4 RELIABILITY	1

3.1.5 MAINTAINABILITY	1

3.2 EQUIPMENT DEFINITION	1

3.2.1 Definition of Suppressor Assemblies to be Provided	1

3.2.2 Spare Parts to be Provided	4

3.3 GENERAL DESIGN FEATURES	4

4.0 TEST AND INSPECTION REQUIREMENTS	5

5.0 QUALITY ASSURANCE REQUIREMENTS	6

5.1 SUBCONTRACTOR'S RESPONSIBILITY FOR CONFORMANCE	6

5.2 CHANGES TO PRINCETON APPROVED DOCUMENTS	6

5.3 INTERCHANGEABILITY	6

5.4 CALIBRATION OF TEST AND MEASURING EQUIPMENT	6

5.5 RELEASE FOR SHIPMENT FORM	6

5.6 INSPECTION & TEST REPORTS	6

5.7 PPPL RECEIVING/ INSPECTION	6

5.8 GENERAL PURCHASE ORDER REQUIREMENTS	7

6.0 DOCUMENTATION REQUIREMENTS	7

8.0 DELIVERABLES	7

9.0 WARRANTY	8

1.0 SCOPE

Subcontractor shall supply Surge Suppressor Assemblies for use on coil systems of National Spherical Torus Experiment (NSTX).

2.0 APPLICABLE DOCUMENTS

a.	IEEE Standard 141- 1993  for Suppressors

b.	National Electric Code

3.0 REQUIREMENTS

3.1 PERFORMANCE REQUIREMENTS

3.1.1 PERFORMANCE CHARACTERISTICS

The Surge Suppressors shall operate in DC Power Circuits, connected across coils which are powered by thyristor rectifiers.

3.1.2 ENVIRONMENTAL

Maximum Ambient Temperature:  40° C

Minimum Ambient Temperature: 10° C

Humidity: 100%,

Magnetic fields:  NA

3.1.3 DESIGN LIFE

The NSTX Machine is designed to operate for 15 years. The circuits will be pulsed for 5 seconds every 300 seconds for 8 consecutive hours per day. All suppressors are to be designed on this basis.

3.1.4 RELIABILITY

Subcontractor shall provide typical failure rates for the products quoted.

3.1.5 MAINTAINABILITY

Subcontractor to provide periodic testing requirements and other maintenance requirements.

3.2 EQUIPMENT DEFINITION

3.2.1 Definition of Suppressor Assemblies to be Provided

Required Suppressor Assemblies are listed in Table 3.2.1-1. Corresponding circuit diagrams are given in Figures 3.2.1-1, -2, -3, -4.

Table 3.2.1-1: List of Required Suppressor Assemblies

| Item # | # Req'd | Line-Line Voltage (kV DC) (Note 1) | Line-Ground Voltage, Nominal (kV DC) (Note 1) | Line-Ground Voltage, Max. (kV DC) (Note 2) | MCOV (kV DC) (Note 3) | #legs per encl'sre | Energy Absorb. (kJ) per leg (Note 4) | Construction per leg (Note 5) | Encl'sre |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| 1 | 1 | 1.0 | 0.5 | 1.0 | 0.5 | 2 | 6.75 | 5 parallel LPC-11856-39 | NEMA 12 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| 2 | 2 | 2.0 | 1.0 | 2.0 | 1.0 | 2 | 12.5 | 5 parallel LPC-11851-11 | NEMA 12 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| 3 | 6 | 2.0 | 2.0 | 4.0 | 1.0 | 3 | 12.5 | 5 parallel LPC-11851-11 | NEMA 12 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| 4 | 2 | 2.0 | 1.0 | 2.0 | 1.0 | 2 | 75.0 | 30 parallel LPC-11851-11 | NEMA 4 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

Notes:

1) Pulsed voltage, 5 seconds on, once every 300 seconds.

2) Fault voltage in case of ground on opposite terminal, maximum duration 0.1 seconds

3) Maximum Continuous Operating Voltage

4) Non-repetitive (assume sufficient time to cool to ambient temperature between events).

5) Parallel modules indicated are for each leg.

6) LPC stands for Lightning Protection Corporation, 5750 Thornwood Dr., Goleta, CA 93117 (phone: 805-967-4577). Subcontractor may propose equivalent with V-I characteristic equal to that of the specified LPC part number.

Figure 3.2.1-1: Item #1 Suppressor Assembly Circuit Diagram

Figure 3.2.1-2: Item #2 Suppressor Assembly Circuit Diagram

Figure 3.2.1-3: Item #3 Suppressor Assembly Circuit Diagram

(Two assemblies shown in typical circuit configuration)

Figure 3.2.1-4: Item #4 Suppressor Assembly Circuit Diagram

(Two assemblies shown in typical circuit configuration)

3.2.2 Spare Parts to be Provided

In addition to the Suppressor Assemblies, the following additional spare parts shall be provided:

- Five (5) type LPC-11856-39 modules (or equivalent as may be substituted per  3.2.1)

- Ten (10) type LPC-11851-11 modules (or equivalent as may be substituted per  3.2.1)

3.3 GENERAL DESIGN FEATURES

a. Where series parallel suppressors are used they shall be closely matched to promote balanced current sharing.

b. Each module shall be interconnected to the respective "+" and "-" terminals with a fuse adequately rated to safely pass the intended pulse currents.

c. All modules shall be suitable for bipolar operation.

d. Design shall be such that the failure of one parallel unit shall not cause failure of the other units in the circuit.

e. The suppressors shall be designed to fail in a short circuit (low impedance) condition. This characteristic needs to be confirmed in writing by the Subcontractor.

f. Typical suppressor parameters, including the voltage vs. current (V-I) characteristics, capacitance, inductance, and resistance shall be provided, including typical range of variations.

g. Subcontractor may propose modules with superior protection capability.

3.4 General Construction Features

a. Each Suppressor Assembly shall be provided with an enclosure (enclosure types listed in Table 3.2.1-1) with hinged cover and provision for cable entry from the top. Subcontractor shall provide dimensions of proposed enclosures with his proposal. Size should allow for future addition of 20% additional modules. Enclosures shall be painted ANSI Grey.

b. Each Suppressor Assembly shall have three terminals, two for the line connections and one for the ground connection.

c. The two line terminals shall be located with the enclosure, mounted on insulators, suitably rated for the voltage levels listed in Table 3.2.1-1, and marked (+) and (-).  The line terminals shall be provided with mechanical screw connectors to accommodate cables, entering the enclosure from the top, up to size 1/0 AWG.

d. The ground terminal shall consist of single metallic plate insulated from the enclosure. The ground terminal shall be provided with mechanical screw connector to accommodate cable, entering the enclosure from the top, up to size 1/0 AWG.

e. All wiring and connections shall be of shortest lengths possible to minimize impedance.

f. The physical arrangement of the modules shall provide for heat transfer and natural cooling during operation.

g. Generally accepted industry practice shall be adopted for all wiring, insulators and hardware.

h. The use of any materials containing PCBs is not acceptable

4.0 TEST AND INSPECTION REQUIREMENTS

a.  Parallel units shall be closely matched. Subcontractor shall provide description of his method for matching the devices for PPPL approval.

b. First article of each item listed in Table 3.2.1-1 shall be inspected and approved by PPPL prior proceeding with remaining articles. Sequence of fabrication shall be such that first articles of each item are available for inspection during one visit to Subcontractor's facility.

5.0 QUALITY ASSURANCE REQUIREMENTS

5.1 SUBCONTRACTOR'S RESPONSIBILITY FOR CONFORMANCE

Neither PPPL's review and/or approval of Subcontractor's documents nor PPPL's inspection of Subcontractor's items or services shall relieve the Subcontractor of responsibility for full compliance with requirements of the purchase order/contract.

5.2 CHANGES TO PRINCETON APPROVED DOCUMENTS

Revisions or changes by the Subcontractor to documents approved by PPPL shall be reviewed and approved by PPPL prior to use.

5.3 INTERCHANGEABILITY

Subcontractor shall assure that like deliverable end items are interchangeable.

5.4 CALIBRATION OF TEST AND MEASURING EQUIPMENT

Inspections and tests shall be performed using properly calibrated measuring and test equipment. Subcontractor shall have in its possession the necessary equipment to perform the required inspections and tests. Calibration standards shall be traceable to the National Institute for Standards and Technology (NIST) or equivalent. Reference standards shall only be used for calibration and verification unless it is demonstrated that their performance as reference standards has not been invalidated. Subcontractor shall impose these calibration requirements on subtier suppliers.

5.5 RELEASE FOR SHIPMENT FORM

Subcontractor shall have a signed "Product Quality Certification and Shipping Release" Form to be provided by PPPL's Quality Assurance Representative prior to acceptance of procured items or services for full or partial shipment. PPPL reserves the right to refuse to accept shipments unless accompanied by a signed "Shipping Release" Form.

5.6 INSPECTION & TEST REPORTS

Copies of the original reports of all required inspections, examinations, and tests, properly validated by authorized personnel shall be provided with each shipment.  One copy is to be provided with the Shipping Release request.

5.7 PPPL RECEIVING/ INSPECTION

PPPL will perform Receiving Inspection on items or services supplied by Subcontractor, using either a sampling plan or 100% inspection. Discrepant items or services will be rejected and returned to Subcontractor or reworked by PPPL.  Costs caused by rejects will be charged to Subcontractor.

5.8 GENERAL PURCHASE ORDER REQUIREMENTS

Material(s) and/or product(s), including those components, parts, and materials, which are permanently installed into systems, sub-systems, and/or assemblies, etc. furnished under this purchase order/subcontract, shall be new and unused. Parts and components that have been rebuilt, refurbished, or modified are specifically prohibited unless approved by PPPL in writing.

Subcontractors (Suppliers) found to be supplying any of the following will be reported to the Office of the Inspector General, U.S. Department of Energy.

•	Remanufactured, rebuilt, or used parts represented as new

•	Counterfeit parts (fraudulently labeled or marked with another manufacturer’s name).

•	Misrepresented parts.

6.0 DOCUMENTATION REQUIREMENTS

Documentation shall be provided as delineated in the following table (one original and one duplicate copy of each document shall be provided unless otherwise specified herein).

| Ref. Section | Item | Due |
| --- | --- | --- |

| 3.1.4 | Typical failure rates | With proposal |
| --- | --- | --- |

| 3.1.5 | Testing and maintenance recommendations | With proposal |
| --- | --- | --- |

| 3.2.1 | Substitutes for LPC products, if any | With proposal |
| --- | --- | --- |

| 3.3.e | Confirmation that suppressors fail shorted | With proposal |
| --- | --- | --- |

| 3.3.f | Suppressor parameters | With proposal |
| --- | --- | --- |

| 3.3.g | Proposal for alternate suppressor selection, if any | With proposal |
| --- | --- | --- |

| 3.4.a | Enclosure dimensions | With proposal |
| --- | --- | --- |

| 4.0.a | Description of method for matching devices | With proposal |
| --- | --- | --- |

| 5.5 | Shipping Release Form | Prior to Shipments |
| --- | --- | --- |

8.0 DELIVERABLES

Deliverable items shall include the following.

a. Surge Suppressor Assemblies listed in Table 3.2.1-1.

b. Spare modules as delineated in 3.2.2.

c. All documentation listed in Section 6.0.

9.0 WARRANTY

Subcontractor shall warranty the product for one year and shall replace the units if there are manufacturing defects.

PRINCETON UNIVERSITY

PLASMA PHYSIC LABORATORY—PPPL

| PRODUCT QUALITY CERTIFICATION AND SHIPPING RELEASE |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |

| PROJECT | ITEM DESCRIPTION |  |  | SHIPMENT NUMBER |  |
| --- | --- | --- | --- | --- | --- |

| PPPL SUBCONTRACT/ ORDER NO. | REV. | ITEM NO. | SUPPLIER REFERENCE NO. | REV. | QUANTITY SHIPPED |
| --- | --- | --- | --- | --- | --- |

| SUPPLIER'S CERTIFICATION This is to certify that the products and services identified herein have been produced under a controlled quality assurance program and are in conformance with the procurement requirements including applicable codes, standards and specifications as identified in the above-referenced documents unless noted below. Any supporting documentation will be retained in accordance with the procurement requirements. SIGNED: ______________________________________ DATE: _____________ TITLE: _______________________________ COMPANY: _______________________________ |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |

| PPPL (AUTHORIZED REPRESENTATIVE) SHIPPING RELEASE This is to certify that evidence supporting the above Supplier's Certification statement has been audited and no product/service nonconformances from procurement requirements have been found unless noted below. This product/service is hereby released for shipment. This section serves as the Quality Assurance release for the above-described product for shipment. It does not constitute an acceptance thereof and does not relieve the Subcontractor, Manufacturer or Contractor of any and all responsibility or obligation imposed by the purchase contract. It does not waive any rights the Purchaser may have under the purchase contract, including the Purchaser's right to reject the above described material upon discovery of any deviations from requirements of the purchase contract, drawings and specifications. |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |

| NONCONFORMANCES FROM PROCUREMENT QUALITY REQUIREMENTS: |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |

| REMARKS/PRODUCT SERIAL NUMBERS: |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |

| BY PPPL QA REPRESENTATIVE (OR DESIGNEE) |  |  |  | DATE |  |
| --- | --- | --- | --- | --- | --- |