13-970213-JMS-01

TO: 		Distribution

FROM:  	J. Spitzer
SUBJECT:  	Summary Description of TF, OH and PF Connection Schemes

References:

1) NSTX Memo:  72-9702130-SMK-01 "STRAY FIELDS IN NSTX"

2) NSTX Memo:  13-970203-CLN-01 "SUMMARY DESCRIPTION OF OH AND PF COILS"

NSTX  Drawings

13.E.0001.0 - OH Coil /Tension Tube Final Assembly Section @ 0° and 180°.

13.E.0002.0 - OH Coil /Tension Tube Final Assembly Section @ 90° and 270°.

13.E.0003.0 - OH Coil /Tension Tube Final Assembly End View Sections.

13.E.0007.0 - PF1b Coil Assembly End Winding Detail.

13.E.0013.0 - PF1a Coil Sections Showing Transitions and Leads.

13.E.0015.0 - Conductor/Insulation Arrangement, TF Inner Core Assembly.

13.E.0101.0 - Centerstack Top @ 0° and 90° Layout.

13.E.0102.0 - Centerstack Bottom @ 0° and 90° Layout.

TF Connections

In the earlier NSTX design the toroidal field was supplied by 12 coils made up of six turns each.  The inner TF coil bundle was comprised of (72) conductors arranged in four layers using four different conductor cross-sections.  Connection of the inner conductors to the outer legs was made by bending the ends of each conductor and brazing on a connector plate. This bending had to be accomplished after the bundle was inserted into the centerstack.  The relocation of NSTX to D-site and subsequent use of the D-site power supplies has permitted redesign of the TF coil system.  This new configuration has greatly simplified the TF lead arrangement.

The TF coil system is now comprised of 12 coils with three turns each.  The Inner TF bundle is made up of an inner layer of (12) pie-shaped copper conductors surrounded by an outer layer of (24) trapezoidal shaped pieces of copper. The copper bars are cooled via copper cooling tubes soft-soldered into grooves (13.E0015.0).  The outer layer conductors are of constant cross-section along their entire lengths.  The conductors of the inner layer are cut in profile with slight radial “flags” on both ends.  This extension of the turns allows the bolting surfaces for both inner and outer layers to be located at the same diameter. With this arrangement no part of the inner TF bundle extends in diameter beyond the inner diameter of the OH solenoid tension cylinder.

At the ends of the Inner TF bundle, flags are bolted to each TF turn (13.E0101.0, 13.E0102.0).  These flags extend radially outward creating sufficient spacing between the bars to permit the connections to the outer legs to be made.  The flags, which are 1” x 5” in cross-section, will be machined and formed from CDA-104 copper plate.  They are cooled primarily by conduction to the adjacent water-cooled inner and outer legs.  The flags are mounted within a hub assembly which provides support for the flags and the load path for transmitting the torque to the umbrella structure of the vacuum vessel.

The resistance of a copper-copper joint such as this is a function of the applied pressure, Figure 2 .  The NSTX joint was designed with a nominal contact pressure of 2000 psi, which is close to the “knee” of the curve where little is gained in decreased joint resistance with increasing bolt load. The joint will be silver plated to further enhance the conductivity of the joint and to provide stable contact resistance.  Preliminary measurements on a mockup of the NSTX joint at 2000 psi confirm the results shown in Figure 1 for the copper to copper condition, while the silver plated joint exhibits roughly four to five times improved conductivity.

Fig. 1:  Behavior of  Joint Resistance as a Function of Joint Pressure

In addition to contact resistance effects, local joint heating is influenced by the variation in current density as the current leaves the inner leg and enters the flag. As described earlier, on the inner turns of the inner TF bundle the copper conductor extends radially outward at the upper and lower ends beyond the basic cross section, so that the current makes the turn from axial to radial directions prior to entering the joint.  However, on the outer turns of the inner legs, because the OD of the bundle cannot exceed the ID of the tension tube into which it must be inserted, this feature is not available. Therefore the outer turns are the worst case as the local heating effect of the current bunching is combined with that of the contact resistance heating.

Based on preliminary joint resistance measurements and 2-d transient electrical/thermal simulations, the silver plated joint provides the required conductivity to limit the local heating to ≤ 140C.  Worst case conditions result from the Bt = 0.6T case, where the pulse time is much shorter than the nominal case and less time is available for heat diffusion.

Although the supporting mechanical structures are being designed to minimize the variation in pressure on the joint under thermal/mechanical load, additional joint resistance measurements on the mockup are underway to determine what level of axial and torsional forces are required to produce a measurable variation in contact resistance. A tentative allowable contact resistance of 2µΩ-in2 has been selected for the design.

Four 5/16”, A286 bolts, with their length extending the full length of the flag, provide elastic preload on the joint which will track thermal expansions and variations in axial loads.  These bolts are “body bound” (i.e., tight fitting) at the joint interface so they react shear loads without slippage.  They are torqued to provide a preload of 2000 psi.   Stainless steel “Keensert” thread inserts are used to provide a hardened bolt interface with improved pull-out strength.  Tests indicate a pull-out strength of ~6000 lbs.

The torque restraint structure , in conjunction with the body bound bolts, keep the joint fixed and clamped under virtually constant pressure throughout the operating cycle.   Table 1 lists the major features of the bolted joint.

Table 1: TF Bolted Joint Features

| Feature | Description |
| --- | --- |

| Size & Number of Bolts | (4) 5/16" bolts |
| --- | --- |

| Bolt Material | A286 |
| --- | --- |

| Bolt Length | 11 in. |
| --- | --- |

| Nominal Joint Pressure | 2000 psi |
| --- | --- |

| Allowable Contact Resistance | 2µΩ-in2 |
| --- | --- |

| Average Current Density @ 71.6kA | 14.3kA/in2 |
| --- | --- |

| Load per Bolt | 2500 lb |
| --- | --- |

| Axial Stress in Bolts | 43000 psi |
| --- | --- |

| Shear Stress in Bolts | 2300 psi |
| --- | --- |

| Pullout Yield Load for Insert | 5000 lb |
| --- | --- |

| Factor of Safety for Pullout | 2 |
| --- | --- |

Connection between the flags and outer legs is accomplished using demountable connectors.  These are provided to permit servicing of the CS ceramic insulators without removal of the outer legs.  The connectors take the shape of a flexible strap which is formed by winding tin plated copper strip into a coil, and then hydraulically flattening it.  The finished strap which is 1” x 5” in cross-section is connected via bolted connections using Belleville washers and stainless steel backing plates.  Current density and heating within the links is relatively low; consequently, direct water cooling is unnecessary.  The resultant flexibility provides mechanical isolation between the connectors and the radial loads resulting from the magnetic force on the outer legs.

Turn to turn transitions for connecting the TF coils in series are also accomplished by these links.   Some of the transitions are made on the upper level, and some on the lower.  At each level, some of the transitions proceed clockwise in a toroidal direction and others anti-clockwise.  A schematic of the overall series connection of the TF is shown in Figure 2. By careful adjustment of the angle of the central bundle with respect to the outer legs the net toroidal current component, and resultant field error, is nullified Reference 1.  Figure 3 illustrates the TF system with a typical arrangement of the TF flags and demountable connectors shown.

OH and PF Connections

The OH and PF1 coils have also been redesigned.  Details of the new designs are presented in Reference 2.  The OH coil now uses a constant cross-section conductor which is wound two-in-hand.  This approach eliminates the transition regions at the end of the coils, and the associated braze joints, where in the previous design the conductor cross-section increased as well as the need for the OH2 coil.  The two in hand winding does, however, add complexity to the OH coil connections.

Figure 3 - TF System General Arrangement

The eight conductor paths of the OH solenoid (four layers of two-in-hand wound conductors) are electrically connected in series while each is cooled separately.  The power supply bus bars for the OH coil are located at the bottom of the centerstack.  The conductors of the OH solenoid are electrically connected connected in series.  Figure 4 is a schematic representation of the OH connections.

At the ends of the solenoid the four layers are staggered in height (inner layer highest and the outer layer lowest) so that the leads can be brought out on top of each other to minimize stray fields.  The lead pairs are brought radially out from the winding at 0°, 90°, 180° and 270°.  At the top these lead pairs are connected using jumpers.  Three of the four leads at the bottom of the solenoid bundle are also connected using jumpers.  The fourth pair connects to the power supply.   Cooling water is supplied for each of the eight conductors at the bottom of the machine with the returns located at the jumpers at the top of the machine (13.E0001.0, 13.E0002.0, 13.E0003.0, 13.E0101.0, 13E0102.0).

The current design uses two PF1a coils, one located around the OH solenoid at the top and one located at the bottom (13.E0013.0).  PF1b is located at the bottom of the machine.  Each of these coils will use two connectors; one for power and water supply the other for return (13.E0007.0).  As in the OH solenoid the leads are brought out with one on top of the other to minimize stray fields.

Distribution:

J. Citrolo	P. Heitzenroeder		C. Neumeyer	NSTX File

1From Copper Development Association (CDA) publication "Copper for Busbars", ch. 5, p. 82