13-001108-CLN-01

TO: DISTRIBUTION

FROM: C NEUMEYER

SUBJECT: TF AS-BUILT CIRCUIT PARAMETERS

Reference:

[1] NSTX-CALC-13-2, “TF Coil Parameters”

[2] NSTX-CALC-13-15, “Water Cooled Flex Cable Thermal/Hydraulic Calculation”

[3] NSTX-CALC-13-18, “TF As-Built Circuit Parameters”

This memo (which is also filed in the ref. [3] calculation with supporting documents) provides a reference for the as-built TF circuit parameters.

Equivalent circuit is shown below.

Resistance values are derived in the following spreadsheet.

| Element | # Name | Data | Value |  | Reference |
| --- | --- | --- | --- | --- | --- |
| Inner Legs | Rcinner |  | 4.680 | mΩ | Calculated |
| Outer Legs | Rcouter |  | 1.090 | mΩ | Calculated |
| Joints, Flags, Flexs etc. | Rcmisc |  | 0.486 | mΩ | Calculated |
| Subtotal | Rcoil |  | 6.256 | mΩ | Calculated |
| Flex Cable, Bus Bar, etc. | Rflex-bus |  | 0.100 | mΩ | Calculated |
| Subtotal |  |  | 6.356 | mΩ |  |
| Transition Area to Test Cell | Rta-ntc |  | 0.610 | mΩ | Measured |
| SDS to Transition Area | Rsds-ta | =2*(0.304+0.292+0.285+0.28+0.298+0.287+0.279+0.279)/8 | 0.576 | mΩ | Average of Measurements |
| Nominal Subtotal |  |  | 7.542 | mΩ |  |
| Test Shot Data: R=V/I |  | =400/53050 | 7.540 | mΩ | Derived from Shot Data |
| Delta |  |  | -0.002 | mΩ |  |
| Delta |  |  | -0.024 | % |  |
| Vps open circuit | Voc |  | 1012.850 | Volt | Basic Rating |
| Test Shot Data: R=(Voc-V)/I |  | =(Voc-777)/50 | 4.717 | mΩ |  |
| Requivalent per branch |  |  | 18.868 | mΩ |  |
| Power Supply Branch Inc'l Clr | Rps-sds+Rclr | =(2.47+2.44+3.3+2.91)/4 | 2.780 | mΩ | Average of Measurements |
| Ips*f/60 |  |  | 13541.667 |  |  |
| Power Supply Requivalent | Rpsequiv |  | 16.056 | mΩ | Calculated |
| Nominal Subtotal |  |  | 18.836 | mΩ |  |
| Actual Subtotal |  |  | 18.868 | mΩ | Derived from Shot Data |
| Delta |  |  | 0.032 | mΩ |  |
| Delta |  |  | 0.171 | % |  |
| 2P ∑R |  |  | 16.974 | mΩ |  |
| 4P ∑R |  |  | 12.257 | mΩ |  |
| 2P ∑Resistance-Rinnerlegs-CLRs-RPSS |  |  |  | 3.766 | mΩ |  |
| 4P ∑Resistance-Rinnerlegs-CLRs-RPSS |  |  |  | 3.313 | mΩ |  |

The following points are noted:

- Coil resistance calculations are from ref. [1] and are consistent with the measurements made during commissioning by J. Chrzanowski (total 6.31mΩ at coil terminals vs. 6.26mΩ calculated).

- Resistance values are at 20oC. Coil inner leg resistance varies considerably during a pulse.

- Water cooled flex cable resistances were calculated  in ref. [2] at 90µΩ. Here an additional 10µΩ is added for the air cooled copper bus run.

- The combined total resistance estimate, up to the SDS cabinets, where the voltage measurements are made, agrees very well with R = V/I   where V is the measured flat top voltage during a 4.5kG test shot.

- Using curve fit data developed by N. Fromm during the TFTR 6T operations the power supply voltage, for 4 sections active on a feeder with a 0.5Ω feeder reactor, is:

V = 1012.85-0.018818*I’+2.4386e-7*I’^2

Where I’ = I*freq/60

At 65Hz, 50kA/4 parallels the equivalent resistance is of order 16mΩ.

- Using the above power supply equivalent resistance along with other measurements of the resistances on the power supply side of the SDS, the combined total resistance estimate, down to the SDS cabinets, where the voltage measurements are made, agrees very well with R=(Voc-V)/I, where Voc is the power supply open circuit voltage, V is the measured voltage just prior to flat top when the power supply is fully on (=0o) and I=50kA, during a test shot.

- Total effective resistances are indicated in the table for the case of 2 and 4 parallel TF operation.

- The data entered in the PSRTC for external circuit resistance (ECR) excludes that resistance associated with the coil inner legs, the power supply equivalent resistance, and the CLRs. Therefore the last set of values indicated in the table are the appropriate PSRTC entries for the 2 and 4 parallel cases.

- Stray inductance is attributable to the cable run.

- With the above data the PSRTC simulation results are in excellent agreement with the field measurements.

cc:	E Baker	M Bell		D Gates	R Hatcher	R Marsala	M Ono

S Ramakrishnan		A Von Halle	M Williams	NSTX File