PRINCETON UNIVERSITY				13-980626-TM-01

Plasma Physics Laboratory:

Fabrication, Operations and Maintenance Division

To: J. Chrzanowski (WBS 1 Manager)	Date:  June 26, 1998

From: Thomas G. Meighan			Subject: Everson Electric 									Vendor Visit June 									24&25, 1998

_____________________________________________________________

INTEROFFICE MEMORANDUM

.

On June, 24 & 25, 1998, John Boscoe (PPPL Quality Control) and I visited Everson Electric. The purpose of this trip was to inspect the ground wall insulation and witness the final test of the NSTX OH Coil. I met with Chuck Hallquist (project engineer).

We were able to inspect the ground wall before painting the ground wall conductive paint.  The ground wall looks extremely good, they did an excellent job.  Both the Megger and Hi-pot test of the coil to ground (Tension tube and conductive ground plane) were very good with a reading of . 5 micro amp's leakage current at 13,000 volts applied.  The Hydrostatic test was also good with Zero pressure drop at 609 psi after 37 minutes. We also went over the documentation package with Everson Quality Control to make sure that it is in order.

Good news on the Outer TF coils. Everson has a company that can do the rolling operation of the outer conductors. They had them bend a trial piece on Tuesday and I saw it when it arrived back at Everson. It looks real good with only a total of 50 thousands keystoneing across the total width of the conductor. So it looks like they can start that phase of the job real soon.

In conclusion, it was a real upbeat trip. The hydrostatic and electrical test were good and the coil looks great. Everson is still planing on shipping the coil on Monday June 29, 1998.

Cc	P. Heitzenroeder

F. Malinowski

C. Neumeyer

M. Ono

G. Pitonak

L. Sutton

C. Such

M. Williams