51-960509-HK-01

TO: C. NEUMEYER

FROM: H. W. KUGEL

SUBJECT: NEUTRAL BEAM AC POWER REQUIREMENTS

1.0 OVERVIEW

An NSTX Upgrade could have from 4 to 8 MW of neutral deuterium (0D) heating using either, 4 PBX-M Neutral Beamlines (at 2 MW  per beamline) or 2 ATF Neutral Beamlines (at 2 MW per beamline). In the case of PBX-M NBI, which should apply also if ATF Neutral Beamlines are used, the power requirements are as follows:

2.0 NEUTRAL BEAM POWER REQUIREMENTS

2.1 Switchyard

The Ion Source Accel Grid  supply is a voltage multiplier. NBI uses a steady AC voltage from the yard and converts it to DC and multiplies. Approximately 25 to 27 KV AC is taken from the yard. The raw AC current value is unavailable at this time, however, other associated numbers are given below. This corresponds to the fixed output from the final tap-changer transformer that feeds the NB Rectifiers. That voltage is present continuously, as soon as, we close the breaker. Then, depending on the firing phase angle, we can obtain 15 to 60 KV DC output from the NB Rectifier.

2.2  Ion Source Input Power and Injected Neutral Beam Power

The Ion Source perveance is different for hydrogen and deuterium. This changes the electrical operating characteristics with species gas.  In addition, due to the neutralization cross section, 0D NBI is more efficient than 0H NBI. The resultant power requirements at maximum power output are:

Maximum Power Hydrogen NBI

Input per Ion Source 	= 50 KV x 100 A = 5 MW

Injected per beamline      	= 1.5 MW

Transmission		= 0.30 @ 50 keV

For 4 NBI Systems

Total Input to Ion Sources	= 4 x 5 MW = 2 0 MW

Total injected NBI power	= 4 x 1.5 MW = 6 MW

Maximum Power Deuterium NBI

Input per Ion Source 	= 50 KV x 70 A = 3.5 MW

Injected per beamline         = 2 MW

Transmission		= 0.57 @50 keV

For 4 NBI Systems

Total Input to Ion Sources	= 4 x 3.5 MW =14 MW

Total injected NBI power	= 4 x 2 MW = 8 MW

cc:

M Ono

NSTX File