52-960506-MNA-02

To:		Distribution

From:		M. Awad

Subject:	MG Simulation with variable TF Coil Resistance

=============================================================

Attached are the MG computer simulation with the effect of the TF coil resistance vary based on the following equation:

R = (0.020874 + rb) + 3.3314e-12x+ 3.64e-22*x*x

where

R = Total TF coil resistance

x = ∫ i2(t)dt

rb = max. bus resistance (.000673Ω)

Summary of the results and comparison with fixed TF coil resistance:

| Category | 3.2 KG @ 5 Sec. | 6.4 KG @ .6 Sec. |
| --- | --- | --- |

| TF Coil Resistance | Fixed | Variable | Fixed | Variable |
| --- | --- | --- | --- | --- |

| Load Current (KADC) | 17.7 | 17.7 | 35.4 | 35.4 |
| --- | --- | --- | --- | --- |

| Time to reach flat top (seconds) | .8 | 1.12 | 1.2 | 1.288 |
| --- | --- | --- | --- | --- |

| Time from end of FT to 0 current (sec) | .7 | .8 | 1.0 | 1.3 |
| --- | --- | --- | --- | --- |

| Min. % speed | 94.2 | 93.4 | 93.5 | 92.5 |
| --- | --- | --- | --- | --- |

| Total I2t (109 amp2.sec) | 1.72 | * 1.704 | 1.857 | 1.8662 |
| --- | --- | --- | --- | --- |

| ESW (I2t/I2) | 5.438 | 5.445 | 1.4697 | 1.4723 |
| --- | --- | --- | --- | --- |

| Max. load voltage under normal op. VDC | 946 | 873.98 | 1461.4 | 1441.9 |
| --- | --- | --- | --- | --- |

| Min. load voltage under normal op. VDC | - 604 | - 410.28 | - 826 | - 566.44 |
| --- | --- | --- | --- | --- |

| Max. volt / coil under normal op. VDC | 78.8 | 72.8 | 121.8 | 120.2 |
| --- | --- | --- | --- | --- |

| Max. volt / turn under normal op. VDC | 13.14 | 12.14 | 20.3 | 20. |
| --- | --- | --- | --- | --- |

| Max volt / coil under fault condition VDC | 307.5 | 252.6 | 610.2 | 505 |
| --- | --- | --- | --- | --- |

| Max volt / turn under fault condition VDC | 51.2 | 42.1 | 101.7 | 84.2 |
| --- | --- | --- | --- | --- |

| ** Energy dissipation MJ | .333 | .276 | 1.33 | 1.1 |
| --- | --- | --- | --- | --- |

| *** Min time to dissipate energy (sec) | .425 | .353 | .425 | .353 |
| --- | --- | --- | --- | --- |

*	Flat top time @17.7 KA within 1% is 4.8 seconds.

**	Energy dissipation under fault condition per pair of .02Ω dump resistors.

***	Minimum time delay required for the safety disconnect to open after opening the resistor breaker.

Conclusion & Recommendation

In reference to the variation of the TF coil resistance as a function of load current and time, the generator controls is capable of regulating the TF current and maintaining it at 17.7 KA for 5 sec within 1%, and at 35.4 KA for .6 sec..

Although the max voltage per coil under fault condition with variable TF coil resistance is less than with fixed resistance, it is recommended to consider the worst condition which is at the beginning of the flat top where the effect of I2t is relatively small and no significant changes in the coil resistance. Thus the TF coil should design to withstand minimum of 610 VDC/coil.

Attachments:

1 - Generator simulation, 3.2 KG with fix TF coil resistance.

2 - Generator simulation, 3.2 KG with variable TF coil resistance

3 - Generator simulation, 6.4 KG with fix TF coil resistance.

4 - Generator simulation, 6.4 KG with variable TF coil resistance.

Distribution:

A. Brooks			C. Neumeyer			NSTX File (S. Citrolo)

P. Heitzenroeder		M. Ono

R. Myslinski			J. Sinnis

D. O'Neill			J. Spitzer