PRINCETON PLASMA PHYSICS LABORATORY

Inter-Office Memorandum

April 07 1997

To									50-970407-SR-01

Distribution

From

S.Ramakrishnan

Subject:	NSTX Power Systems WBS5 - Power Cabling to Coil System

A review meeting was held on April 04 1997 to discuss the proposed alternative route with associated cost and take a decision on the proposed alternative power cable routing.  Following were present.

C. Neumeyer				M.Ono

E. Perry				T. Egebo

L. Dudek

S. Ramakrishnan

The writer presented the details of the cost of the proposed scheme. A comparison spreadsheet of costs projected by (1) Henry Carnevale and (2) by E. Perry was discussed in detail itemwise. The work involved is to clear the way for future power cable routing for NSTX from Waterfall area to the Hot Cell via the Mechanical equipment room giving a corridor of 72" x 42" of clear space all through the route. ( Note that the proposed route has been walked through by both Henry Carnevale and E. Perry who are clearly aware of the requirements. ). If both the cost projections are combined accepting higher of the cost of each item , the resultant cost may increase by < 50 k$ to 388.48k$, from the existing budget provisions in WBS 8 of 344 k$.

The major difference in the two estimates was the cost of providing penetrations. Following penetration work is involved:

a) Provide 6 - 9" penetrations in the Test Cell Floor.

b) Enlarge the existing penetration # 320 in the wall between Test Cell Basement and the Mech. Equipment Room from 39" wide x 31" high to 39" wide and 78" high.

While Henry Carnevale has projected 38.46k$ , E. Perry has 104.92 k$  i.e. a difference of 66.46k$. Henry's estimate was based on some input from a subcontractor (Whisper).

S. Ramakrishnan presented a Purchase Order by J. Chrzanowski , to Whisper awarded and executed in Aug. 92, for making 3 - 5" penetrations and 1 - 8" penetration in the Hot Cell Floor for a total cost of $ 600.

The majority of the review members felt that the projected cost of 104.92 k$ may be high and , It was decided to modify the estimate after a field inspection on the proposed work by a prospective subcontractor.

S. Ramakrishnan conveyed the following:

a) The proposed alternative routing is technically superior even though cable pulling tasks will be more labor intensive with an additional 130 MDs of Technician labor.

b) Requested this routing be approved. T. Egebo pointed out that the potential increase in the  proposed cost is under 50k$ and the Project Engineer can approve the scheme especially because it  is technically superior.

c) Clear passage of about 84" x 42" is required from Waterfall to Hot Cell and all pertinent equipment on the way are to be removed or repositioned, including SF6 detectors etc. (SF6 detectors are no longer required in the TCB since there will be no equipment with SF6.)

d) Cage around the tray system shall be provided in the Test Cell basement with required access doors. (E. Perry conveyed that this has already been budgeted in WBS8 as a separate task)

After reviewing both the technical and cost aspects, M. Ono and C. Neumeyer approved the alternative route for implementation, since the cost increase as proposed is under 50k$.  They however stated that the estimate for penetrations be revisited after getting a subcontractor's input.

S. Ramakrishnan will prepare the authorization package as  the resolution on the CHIT # 5 , generated during the CDR on WBS5 held on February 06 1997. ( This chit requested a review on the proposed route to insure clear space to remove HVEs from the basement).

Following documents are herewith attached:

1.	Copy of documents presented during the review - cost estimate by Henry Carnevale and 	E. Perry. Includes a comparison sheet prepared by S. Ramakrishnan.

2	Resolution of chits generated during the review on March 26 97.

3	Memo from C. Potensky raising the cost estimate by H. Carnevale by $3400 to provide 	for the lifting beams under the platform to maintain the compressors.

4	Memo regarding Estimate changes from E. Perry to resolve Chits 3&4

5	Copy of the purchase order for making one 8" and three 5" penetrations in Hot Cell 	floor in August 92 (from J. Chrzanowski)

CC:

Attendees

C. Ancher

H. Anderson		J.W. Anderson			H. Neilson

J. Corl		J. Sinnis				M. Peng

J. Chrzanowski	A. von Halle				M. Ono

R. Strykowsky	M. Williams				S. Citrolo

B. McCormack	P. Heitzenroeder

C. Potensky		J. Chrzanowski

H. Carnevale

J. Spitzer