PRINCETON PLASMA PHYSICS LABORATORY

Inter-Office Memorandum

March 19 1997

To									50-970319-SR-01

Distribution

From

S.Ramakrishnan

Subject:	NSTX Power Systems WBS5 - Power Cabling to Coil System

Routing for NSTX Coils power cabling is being reviewed. In the original plan the cables were proposed to be routed through the hatch in the test cell floor (south east side). Routing through the hatch on the test cell floor for the tray system will prevent the hatch being put to its originally intended use. Equipment removal from the basement will thus become more difficult. Furthermore part of Test Cell (TC) space will also be called upon for NSTX use.

We are proposing an alternative route which will not require the use of the hatch or portions of the test cell. In this scheme the raceway system will be routed from the Test Cell Basement (TCB) into the Mechanical Equipment Room (MER) and then on to the Hot Cell (HC). See attachment 1 . There was a walk through with Henry Carnavale on FEBRUARY 25 97 , for identifying the tasks of relocation. Henry stated that the necessary modifications /relocation can be made without affecting the overall performance of HVAC / Fire Protection / Misc. system.  An estimate has been provided by Henry  for tasks associated with the relocation of HVAC  & Misc. equipment to clear the way for the tray system. See Attachment 2.

The work involved to clear the way for the routing is given in attachment 3.  Scope of work for the routing task under WBS 8 / TFTR Shutdown tasks,  has to change to reflect the alternative routing proposed and funding has to be reallocated. Also tasks included in the proposed shutdown /dismantling activities have to be changed to include the items as appropriate.

A meeting is proposed to be held on March 26 1997 in Room B 318 at 10:00 hours to discuss the subject and take a decision.

ATTACHMENT 3

If the new proposed routing is adopted the following work is involved under the overall scope of WBS 8 and TFTR Shutdown tasks:

| Sl# | Description | Responsible |
| --- | --- | --- |

| 1 | Relocate HVAC & misc. equipment for FED in that area as needed. | FED |
| --- | --- | --- |

| 2 | Release HVAC penetrations #320 from the Test Cell to the Mech. Equipment Room. This penetration is located between N5 & P4 columns and is 38"wide and 31" high. This has to be enlarged to 38"wide x 72" high. | FED |
| --- | --- | --- |

| 3 | Provide six 9" penetrations from the Mechanical Equipment Room (MER) to the Hot Cell (HC). Will also use an existing opening from MER to the HC about 24" x 31" | FED |
| --- | --- | --- |

| 4 | a) Provide Platforms in MER b) Extend / modify platform above the vacuum pumps in the TC basement. c) Provide cage around the tray system in MER . | FED |
| --- | --- | --- |

| 5 | a) Remove the block wall around the transition area in the East Side and associated doors. b) Provide Cage around the Power Tray system in TC basement including the Transition area and provide doors for access. | ? |
| --- | --- | --- |

| 6 | a) Remove the NB 4 & 5 HVEs. b) Remove NB 2 HVEs so that the dummy load can be positioned in the place occupied by NB2C HVE. c) Remove all the junction boxes / pull boxes / trays associated with the NB 2,4 & 5 d) Remove the SF6 (Systems 5 & 6)detectors and associated panels. | NB |
| --- | --- | --- |

| 7 | Remove the TFTR Bellows Cooling Fan (Spencer fan) and associated piping to clear the way. | ? |
| --- | --- | --- |

| 8 | Remove the RF racks in the TCB near the Transition area. Randy Wilson has stated that these racks will be relocated for NSTX use. | RF |
| --- | --- | --- |

| 9 | Remove the Bumper Limiter Water control panel on the mezzanine over the Vacuum pumps | ? |
| --- | --- | --- |

| 10 | Other Misc. work if any to be identified under WBS 8 |  |
| --- | --- | --- |

Note:

Per Alex Nagy, Glow Discharge equipment will be removed from the platform near the Hatch. Even if the panel is to be retained int he existing position it will not interfere with the tray system.

Distribution:

C. Ancher			P. Heitzenroeder

H. Anderson			C. Neumeyer

J. Corl			E. Perry

D. McBride			L. Dudek

S. Kemp			T. Egebo

F. Beane			A. von Halle

H. Carnevale			J. Levine

A. Nagy			R. Strykowsky

C. Potensky

R. Jeanes

T. O'Connor

B. McCormack

T. Stevenson

cc:

J.W. Anderson		S. Citrolo

H. Neilson

M. Ono			Project Files

M. Peng

J. Sinnis

M. Williams