The symbols and color conventions used for the GUI/displays will follow those used on TFTR “Console” displays and TRECAMS displays.  That is, colored text and symbols representing process equipment will be displayed on a dark background.   Below are some general color rules, followed by an excerpt from the MEDM Reference Manual which describes the use of color for EPICS displays.

- Valves :

- Red indicates a fully CLOSED valve.

- Green indicates a fully OPEN valve.

- Magenta indicates a valve in an indeterminate state.

- Breakers/Switches

- Red indicates a CLOSED switch.

- Green indicates a fully OPEN switch.

- Magenta indicates a switch in an indeterminate state.

- White symbols and text should be avoided since white is the color EPICS uses to represents records/devices which are not operating/communicating properly.

- Text

- Cyan should be used for static text, labels, etc. …

- Green or Black-on-green should be used to indicate normal, safe status.

- Red or White-on-red should be used to indicate abnormal or energized conditions.

# The following  is an excerpt from the MEDM Reference Manual.

# Color Conventions

The following color conventions should be used when creating displays:

# Controls

Any control button, slider, menu, related display, text entry, etc. that makes something happen should be BLUE (second row blue in the MEDM default color palette). This is useful because operators can quickly observe "hot spots" on a display where they can make something happen (change a value, call up another display, etc.). The context or icon of "the blue thing" should adequately convey WHAT will happen if they click on it.

# Text

All text updates should be displayed on a background that allows all alarm colors to be visible (if the alarm dynamic is set). We usually use light gray or dark gray (almost black). Another "RULE OF THUMB" that we tell the operators is "If the text is WHITE, don't believe the reading. The computer cannot communicate to the process variable". Therefore, white static text is discouraged.

Likewise, since RED, GREEN, and YELLOW reflect alarm conditions, these colors should not be used for static text or text updates.

No colors are "disallowed" from being used for graphical images (magnets, waveguides, etc) because it is usually very obvious that these are pictures and NOT dynamic objects.

# Colors in General

• DIN Standards 4844 and 5381 should be followed whenever possible.

• Red is a danger color. It means Halt, Stop, Prohibited, etc.

• Yellow is used as a warning color.

• Green means Safety, OK, On etc.

• Blue is used for giving directions, advice, signs, etc

# Appendix D

# Display Color Conventions