## Signals
CRATE | SLOT | Ch | EPICS Name & MDS tag | MDSplus ENGINEERING tree FCPC branch signal node names | Scale Factor | Comment | TFTR Power Supply
|  |  | EPICS is case-sensitive MDS is not. | full path \ENGINEERING::TOP.EPICS.FCPC.DIGITIZERS: | volts or amps.
2 | 13 | 1 | pc_tf_pss_1s_1p_ia | TF_P1S_1PIA | 6000 a/v | A | ETF1-PSS-1 |  | ETF1-PSS-1 | 799 | A | -6KA/V | A1TB2-2 | A1TB2-1 | TF_P1S_1PIA | pc_tf_pss_1s_1p_ia | 2 | 13 | 1
2 | 13 | 2 | pc_tf_pss_1s_1p_ib | TF_P1S_1PIB | 6000 a/v | B | ETF1-PSS-1 |  | ETF1-PSS-1 | 799 | B | -6KA/V | A1TB2-4 | A1TB2-3 | TF_P1S_1PIB | pc_tf_pss_1s_1p_ib | 2 | 13 | 2
2 | 13 | 3 | pc_tf_pss_1s_1p_va | TF_P1S_1PVA | 300 v/v | A | ETF1-PSS-1 |  | ETF1-PSS-1 | 799 | A | 300V/V | A1TB2-5 | A1TB2-6 | TF_P1S_1PVA | pc_tf_pss_1s_1p_va | 2 | 13 | 3
2 | 13 | 4 | pc_tf_pss_1s_1p_vb | TF_P1S_1PVB | 300 v/v | B | ETF1-PSS-1 |  | ETF1-PSS-1 | 799 | B | 300V/V | A1TB2-7 | A1TB2-8 | TF_P1S_1PVB | pc_tf_pss_1s_1p_vb | 2 | 13 | 4
2 | 13 | 5 | pc_tf_pss_1s_2p_ia | TF_P1S_2PIA | 6000 a/v | A | ETF1-PSS-2 |  | ETF1-PSS-2 | 801 | A | -6KA/V | A1TB2-2 | A1TB2-1 | TF_P1S_2PIA | pc_tf_pss_1s_2p_ia | 2 | 13 | 5
2 | 13 | 6 | pc_tf_pss_1s_2p_ib | TF_P1S_2PIB | 6000 a/v | B | ETF1-PSS-2 |  | ETF1-PSS-2 | 801 | B | -6KA/V | A1TB2-4 | A1TB2-3 | TF_P1S_2PIB | pc_tf_pss_1s_2p_ib | 2 | 13 | 6
2 | 13 | 7 | pc_tf_pss_1s_2p_va | TF_P1S_2PVA | 300 v/v | A | ETF1-PSS-2 |  | ETF1-PSS-2 | 801 | A | 300V/V | A1TB2-5 | A1TB2-6 | TF_P1S_2PVA | pc_tf_pss_1s_2p_va | 2 | 13 | 7
2 | 13 | 8 | pc_tf_pss_1s_2p_vb | TF_P1S_2PVB | 300 v/v | B | ETF1-PSS-2 |  | ETF1-PSS-2 | 801 | B | 300V/V | A1TB2-7 | A1TB2-8 | TF_P1S_2PVB | pc_tf_pss_1s_2p_vb | 2 | 13 | 8
2 | 13 | 9 | pc_tf_pss_1s_3p_ia | TF_P1S_3PIA | 6000 a/v | A | ETF1-PSS-3 |  | ETF1-PSS-3 | 819 | A | -6KA/V | A1TB2-2 | A1TB2-1 | TF_P1S_3PIA | pc_tf_pss_1s_3p_ia | 2 | 13 | 9
2 | 13 | 10 | pc_tf_pss_1s_3p_ib | TF_P1S_3PIB | 6000 a/v | B | ETF1-PSS-3 |  | ETF1-PSS-3 | 819 | B | -6KA/V | A1TB2-4 | A1TB2-3 | TF_P1S_3PIB | pc_tf_pss_1s_3p_ib | 2 | 13 | 10
2 | 13 | 11 | pc_tf_pss_1s_3p_va | TF_P1S_3PVA | 300 v/v | A | ETF1-PSS-3 |  | ETF1-PSS-3 | 819 | A | 300V/V | A1TB2-5 | A1TB2-6 | TF_P1S_3PVA | pc_tf_pss_1s_3p_va | 2 | 13 | 11
2 | 13 | 12 | pc_tf_pss_1s_3p_vb | TF_P1S_3PVB | 300 v/v | B | ETF1-PSS-3 |  | ETF1-PSS-3 | 819 | B | 300V/V | A1TB2-7 | A1TB2-8 | TF_P1S_3PVB | pc_tf_pss_1s_3p_vb | 2 | 13 | 12
2 | 13 | 13 | pc_tf_pss_1s_4p_ia | TF_P1S_4PIA | 6000 a/v | A | ETF1-PSS-4 |  | ETF1-PSS-4 | 821 | A | -6KA/V | A1TB2-2 | A1TB2-1 | TF_P1S_4PIA | pc_tf_pss_1s_4p_ia | 2 | 13 | 13
2 | 13 | 14 | pc_tf_pss_1s_4p_ib | TF_P1S_4PIB | 6000 a/v | B | ETF1-PSS-4 |  | ETF1-PSS-4 | 821 | B | -6KA/V | A1TB2-4 | A1TB2-3 | TF_P1S_4PIB | pc_tf_pss_1s_4p_ib | 2 | 13 | 14
2 | 13 | 15 | pc_tf_pss_1s_4p_va | TF_P1S_4PVA | 300 v/v | A | ETF1-PSS-4 |  | ETF1-PSS-4 | 821 | A | 300V/V | A1TB2-5 | A1TB2-6 | TF_P1S_4PVA | pc_tf_pss_1s_4p_va | 2 | 13 | 15
2 | 13 | 16 | pc_tf_pss_1s_4p_vb | TF_P1S_4PVB | 300 v/v | B | ETF1-PSS-4 |  | ETF1-PSS-4 | 821 | B | 300V/V | A1TB2-7 | A1TB2-8 | TF_P1S_4PVB | pc_tf_pss_1s_4p_vb | 2 | 13 | 16
[9 empty] | ETF1-PSS-5 | 839 | A | -6KA/V | A1TB2-2 | A1TB2-1 | TF_P1S_5PIA | pc_tf_pss_1s_5p_ia | 2 | 17 | 1
2 | 17 | 1 | pc_tf_pss_1s_5p_ia | TF_P1S_5PIA | 6000 a/v | A | ETF1-PSS-5 |  | ETF1-PSS-5 | 839 | B | -6KA/V | A1TB2-4 | A1TB2-3 | TF_P1S_5PIB | pc_tf_pss_1s_5p_ib | 2 | 17 | 2
2 | 17 | 2 | pc_tf_pss_1s_5p_ib | TF_P1S_5PIB | 6000 a/v | B | ETF1-PSS-5 |  | ETF1-PSS-5 | 839 | A | 300V/V | A1TB2-5 | A1TB2-6 | TF_P1S_5PVA | pc_tf_pss_1s_5p_va | 2 | 17 | 3
2 | 17 | 3 | pc_tf_pss_1s_5p_va | TF_P1S_5PVA | 300 v/v | A | ETF1-PSS-5 |  | ETF1-PSS-5 | 839 | B | 300V/V | A1TB2-7 | A1TB2-8 | TF_P1S_5PVB | pc_tf_pss_1s_5p_vb | 2 | 17 | 4
2 | 17 | 4 | pc_tf_pss_1s_5p_vb | TF_P1S_5PVB | 300 v/v | B | ETF1-PSS-5 |  | ETF1-PSS-6 | 841 | A | -6KA/V | A1TB2-2 | A1TB2-1 | TF_P1S_6PIA | pc_tf_pss_1s_6p_ia | 2 | 17 | 5
2 | 17 | 5 | pc_tf_pss_1s_6p_ia | TF_P1S_6PIA | 6000 a/v | A | ETF1-PSS-6 |  | ETF1-PSS-6 | 841 | B | -6KA/V | A1TB2-4 | A1TB2-3 | TF_P1S_6PIB | pc_tf_pss_1s_6p_ib | 2 | 17 | 6
2 | 17 | 6 | pc_tf_pss_1s_6p_ib | TF_P1S_6PIB | 6000 a/v | B | ETF1-PSS-6 |  | ETF1-PSS-6 | 841 | A | 300V/V | A1TB2-5 | A1TB2-6 | TF_P1S_6PVA | pc_tf_pss_1s_6p_va | 2 | 17 | 7
2 | 17 | 7 | pc_tf_pss_1s_6p_va | TF_P1S_6PVA | 300 v/v | A | ETF1-PSS-6 |  | ETF1-PSS-6 | 841 | B | 300V/V | A1TB2-7 | A1TB2-8 | TF_P1S_6PVB | pc_tf_pss_1s_6p_vb | 2 | 17 | 8
2 | 17 | 8 | pc_tf_pss_1s_6p_vb | TF_P1S_6PVB | 300 v/v | B | ETF1-PSS-6 |  | ETF1-PSS-7 | 859 | A | -6KA/V | A1TB2-2 | A1TB2-1 | TF_P1S_7PIA | pc_tf_pss_1s_7p_ia | 2 | 17 | 9
2 | 17 | 9 | pc_tf_pss_1s_7p_ia | TF_P1S_7PIA | 6000 a/v | A | ETF1-PSS-7 |  | ETF1-PSS-7 | 859 | B | -6KA/V | A1TB2-4 | A1TB2-3 | TF_P1S_7PIB | pc_tf_pss_1s_7p_ib | 2 | 17 | 10
2 | 17 | 10 | pc_tf_pss_1s_7p_ib | TF_P1S_7PIB | 6000 a/v | B | ETF1-PSS-7 |  | ETF1-PSS-7 | 859 | A | 300V/V | A1TB2-5 | A1TB2-6 | TF_P1S_7PVA | pc_tf_pss_1s_7p_va | 2 | 17 | 11
2 | 17 | 11 | pc_tf_pss_1s_7p_va | TF_P1S_7PVA | 300 v/v | A | ETF1-PSS-7 |  | ETF1-PSS-7 | 859 | B | 300V/V | A1TB2-7 | A1TB2-8 | TF_P1S_7PVB | pc_tf_pss_1s_7p_vb | 2 | 17 | 12
2 | 17 | 12 | pc_tf_pss_1s_7p_vb | TF_P1S_7PVB | 300 v/v | B | ETF1-PSS-7 |  | ETF1-PSS-8 | 861 | A | -6KA/V | A1TB2-2 | A1TB2-1 | TF_P1S_8PIA | pc_tf_pss_1s_8p_ia | 2 | 17 | 13
2 | 17 | 13 | pc_tf_pss_1s_8p_ia | TF_P1S_8PIA | 6000 a/v | A | ETF1-PSS-8 |  | ETF1-PSS-8 | 861 | B | -6KA/V | A1TB2-4 | A1TB2-3 | TF_P1S_8PIB | pc_tf_pss_1s_8p_ib | 2 | 17 | 14
2 | 17 | 14 | pc_tf_pss_1s_8p_ib | TF_P1S_8PIB | 6000 a/v | B | ETF1-PSS-8 |  | ETF1-PSS-8 | 861 | A | 300V/V | A1TB2-5 | A1TB2-6 | TF_P1S_8PVA | pc_tf_pss_1s_8p_va | 2 | 17 | 15
2 | 17 | 15 | pc_tf_pss_1s_8p_va | TF_P1S_8PVA | 300 v/v | A | ETF1-PSS-8 |  | ETF1-PSS-8 | 861 | B | 300V/V | A1TB2-7 | A1TB2-8 | TF_P1S_8PVB | pc_tf_pss_1s_8p_vb | 2 | 17 | 16
2 | 17 | 16 | pc_tf_pss_1s_8p_vb | TF_P1S_8PVB | 300 v/v | B | ETF1-PSS-8 |  | ETF1-PSS-9 | 879 |  | -6KA/V | A1TB2-2 | A1TB2-1 | TF1_P9C_IA | pc_tf1_pss_9c_ia | 3 | 18 | 1
[9 empty] | ETF1-PSS-9 | 879 |  | -6KA/V | A1TB2-4 | A1TB2-3 | TF1_P9C_IB | pc_tf1_pss_9c_ib | 3 | 18 | 2
[9 empty] | ETF1-PSS-9 | 879 |  | 300V/V | A1TB2-5 | A1TB2-6 | TF1_P9C_VA | pc_tf1_pss_9c_va | 3 | 18 | 3
[9 empty] | ETF1-PSS-9 | 879 |  | 300V/V | A1TB2-7 | A1TB2-8 | TF1_P9C_VB | pc_tf1_pss_9c_vb | 3 | 18 | 4
| spare TF PSS | [7 empty] | ETF1-PSS-A | 881 |  | -6KA/V | A1TB2-2 | A1TB2-1 | TF1_PAC_IA | pc_tf1_pss_ac_ia | 3 | 18 | 5
3 | 18 | 1 | pc_tf1_pss_9c_ia | TF1_P9C_IA | 6000 a/v | A | ETF1-PSS-9 |  | ETF1-PSS-A | 881 |  | -6KA/V | A1TB2-4 | A1TB2-3 | TF1_PAC_IB | pc_tf1_pss_ac_ib | 3 | 18 | 6
3 | 18 | 2 | pc_tf1_pss_9c_ib | TF1_P9C_IB | 6000 a/v | B | ETF1-PSS-9 |  | ETF1-PSS-A | 881 |  | 300V/V | A1TB2-5 | A1TB2-6 | TF1_PAC_VA | pc_tf1_pss_ac_va | 3 | 18 | 7
3 | 18 | 3 | pc_tf1_pss_9c_va | TF1_P9C_VA | 300 v/v | A | ETF1-PSS-9 |  | ETF1-PSS-A | 881 |  | 300V/V | A1TB2-7 | A1TB2-8 | TF1_PAC_VB | pc_tf1_pss_ac_vb | 3 | 18 | 8
3 | 18 | 4 | pc_tf1_pss_9c_vb | TF1_P9C_VB | 300 v/v | B | ETF1-PSS-9 |  | ETF2-PSS-7 | 989 |  | -6KA/V | A1TB2-2 | A1TB2-1 | OH_P2S_1PI | pc_oh_pss_2s_1p_i | 5 | 14 | 1
3 | 18 | 5 | pc_tf1_pss_ac_ia | TF1_PAC_IA | 6000 a/v | A | ETF1-PSS-A |  | ETF2-PSS-7 | 989 |  | -6KA/V | A1TB2-4 | A1TB2-3 | OH_P1S_1PI | pc_oh_pss_1s_1p_i | 5 | 14 | 2
3 | 18 | 6 | pc_tf1_pss_ac_ib | TF1_PAC_IB | 6000 a/v | B | ETF1-PSS-A |  | ETF2-PSS-7 | 989 |  | 300V/V | A1TB2-5 | A1TB2-6 | OH_P2S_1PV | pc_oh_pss_2s_1p_v | 5 | 14 | 3
3 | 18 | 7 | pc_tf1_pss_ac_va | TF1_PAC_VA | 300 v/v | A | ETF1-PSS-A |  | ETF2-PSS-7 | 989 |  | 300V/V | A1TB2-7 | A1TB2-8 | OH_P1S_1PV | pc_oh_pss_1s_1p_v | 5 | 14 | 4
3 | 18 | 8 | pc_tf1_pss_ac_vb | TF1_PAC_VB | 300 v/v | B | ETF1-PSS-A |  | ETF2-PSS-8 | 991 |  | -6KA/V | A1TB2-2 | A1TB2-1 | OH_P2S_2PI | pc_oh_pss_2s_2p_i | 5 | 14 | 5
[9 empty] | ETF2-PSS-8 | 991 |  | -6KA/V | A1TB2-4 | A1TB2-3 | OH_P1S_2PI | pc_oh_pss_1s_2p_i | 5 | 14 | 6
[9 empty] | ETF2-PSS-8 | 991 |  | 300V/V | A1TB2-5 | A1TB2-6 | OH_P2S_2PV | pc_oh_pss_2s_2p_v | 5 | 14 | 7
5 | 14 | 1 | pc_oh_pss_2s_1p_i | OH_P2S_1PI | 6000 a/v | A | ETF2-PSS-7 |  | ETF2-PSS-8 | 991 |  | 300V/V | A1TB2-7 | A1TB2-8 | OH_P1S_2PV | pc_oh_pss_1s_2p_v | 5 | 14 | 8
5 | 14 | 2 | pc_oh_pss_1s_1p_i | OH_P1S_1PI | 6000 a/v | B | 0 |  | ETF2-PSS-3 | 949 |  | -6KA/V | A1TB2-2 | A1TB2-1 | OH_P6S_1PI | pc_oh_pss_6s_1p_i | 5 | 18 | 1
5 | 14 | 3 | pc_oh_pss_2s_1p_v | OH_P2S_1PV | 300 v/v | A | 0 |  | ETF2-PSS-3 | 949 |  | -6KA/V | A1TB2-4 | A1TB2-3 | OH_P5S_1PI | pc_oh_pss_5s_1p_i | 5 | 18 | 2
5 | 14 | 4 | pc_oh_pss_1s_1p_v | OH_P1S_1PV | 300 v/v | B | 0 |  | ETF2-PSS-3 | 949 |  | 300V/V | A1TB2-5 | A1TB2-6 | OH_P6S_1PV | pc_oh_pss_6s_1p_v | 5 | 18 | 3
5 | 14 | 5 | pc_oh_pss_2s_2p_i | OH_P2S_2PI | 6000 a/v | A | ETF2-PSS-8 |  | ETF2-PSS-3 | 949 |  | 300V/V | A1TB2-7 | A1TB2-8 | OH_P5S_1PV | pc_oh_pss_5s_1p_v | 5 | 18 | 4
5 | 14 | 6 | pc_oh_pss_1s_2p_i | OH_P1S_2PI | 6000 a/v | B | 0 |  | ETF2-PSS-4 | 951 |  | -6KA/V | A1TB2-2 | A1TB2-1 | OH_P6S_2PI | pc_oh_pss_6s_2p_i | 5 | 18 | 5
5 | 14 | 7 | pc_oh_pss_2s_2p_v | OH_P2S_2PV | 300 v/v | A | 0 |  | ETF2-PSS-4 | 951 |  | -6KA/V | A1TB2-4 | A1TB2-3 | OH_P5S_2PI | pc_oh_pss_5s_2p_i | 5 | 18 | 6
5 | 14 | 8 | pc_oh_pss_1s_2p_v | OH_P1S_2PV | 300 v/v | B | 0 |  | ETF2-PSS-4 | 951 |  | 300V/V | A1TB2-5 | A1TB2-6 | OH_P6S_2PV | pc_oh_pss_6s_2p_v | 5 | 18 | 7
[9 empty] | ETF2-PSS-4 | 951 |  | 300V/V | A1TB2-7 | A1TB2-8 | OH_P5S_2PV | pc_oh_pss_5s_2p_v | 5 | 18 | 8
5 | 18 | 1 | pc_oh_pss_6s_1p_i | OH_P6S_1PI | 6000 a/v | A | ETF2-PSS-3 |  | ETF2-PSS-5 | 969 |  | -6KA/V | A1TB2-2 | A1TB2-1 | OH_P4S_1PI | pc_oh_pss_4s_1p_i | 5 | 18 | 9
5 | 18 | 2 | pc_oh_pss_5s_1p_i | OH_P5S_1PI | 6000 a/v | B | 0 |  | ETF2-PSS-5 | 969 |  | -6KA/V | A1TB2-4 | A1TB2-3 | OH_P3S_1PI | pc_oh_pss_3s_1p_i | 5 | 18 | 10
5 | 18 | 3 | pc_oh_pss_6s_1p_v | OH_P6S_1PV | 300 v/v | A | 0 |  | ETF2-PSS-5 | 969 |  | 300V/V | A1TB2-5 | A1TB2-6 | OH_P4S_1PV | pc_oh_pss_4s_1p_v | 5 | 18 | 11
5 | 18 | 4 | pc_oh_pss_5s_1p_v | OH_P5S_1PV | 300 v/v | B | 0 |  | ETF2-PSS-5 | 969 |  | 300V/V | A1TB2-7 | A1TB2-8 | OH_P3S_1PV | pc_oh_pss_3s_1p_v | 5 | 18 | 12
5 | 18 | 5 | pc_oh_pss_6s_2p_i | OH_P6S_2PI | 6000 a/v | A | ETF2-PSS-4 |  | ETF2-PSS-6 | 971 |  | -6KA/V | A1TB2-2 | A1TB2-1 | OH_P4S_2PI | pc_oh_pss_4s_2p_i | 5 | 18 | 13
5 | 18 | 6 | pc_oh_pss_5s_2p_i | OH_P5S_2PI | 6000 a/v | B | 0 |  | ETF2-PSS-6 | 971 |  | -6KA/V | A1TB2-4 | A1TB2-3 | OH_P3S_2PI | pc_oh_pss_3s_2p_i | 5 | 18 | 14
5 | 18 | 7 | pc_oh_pss_6s_2p_v | OH_P6S_2PV | 300 v/v | A | 0 |  | ETF2-PSS-6 | 971 |  | 300V/V | A1TB2-5 | A1TB2-6 | OH_P4S_2PV | pc_oh_pss_4s_2p_v | 5 | 18 | 15
5 | 18 | 8 | pc_oh_pss_5s_2p_v | OH_P5S_2PV | 300 v/v | B | 0 |  | ETF2-PSS-6 | 971 |  | 300V/V | A1TB2-7 | A1TB2-8 | OH_P3S_2PV | pc_oh_pss_3s_2p_v | 5 | 18 | 16
5 | 18 | 9 | pc_oh_pss_4s_1p_i | OH_P4S_1PI | 6000 a/v | A | ETF2-PSS-5 |  | ETF2-PSS-1 | 930 |  | -6KA/V | A1TB2-2 | A1TB2-1 | OH_P8S_1PI | pc_oh_pss_8s_1p_i | 18 | 2 | 1
5 | 18 | 10 | pc_oh_pss_3s_1p_i | OH_P3S_1PI | 6000 a/v | B | 0 |  | ETF2-PSS-1 | 930 |  | -6KA/V | A1TB2-4 | A1TB2-3 | OH_P7S_1PI | pc_oh_pss_7s_1p_i | 18 | 2 | 2
5 | 18 | 11 | pc_oh_pss_4s_1p_v | OH_P4S_1PV | 300 v/v | A | 0 |  | ETF2-PSS-1 | 930 |  | 300V/V | A1TB2-5 | A1TB2-6 | OH_P8S_1PV | pc_oh_pss_8s_1p_v | 18 | 2 | 3
5 | 18 | 12 | pc_oh_pss_3s_1p_v | OH_P3S_1PV | 300 v/v | B | 0 |  | ETF2-PSS-1 | 930 |  | 300V/V | A1TB2-7 | A1TB2-8 | OH_P7S_1PV | pc_oh_pss_7s_1p_v | 18 | 2 | 4
5 | 18 | 13 | pc_oh_pss_4s_2p_i | OH_P4S_2PI | 6000 a/v | A | ETF2-PSS-6 |  | ETF2-PSS-2 | 931 |  | -6KA/V | A1TB2-2 | A1TB2-1 | OH_P8S_2PI | pc_oh_pss_8s_2p_i | 18 | 2 | 5
5 | 18 | 14 | pc_oh_pss_3s_2p_i | OH_P3S_2PI | 6000 a/v | B | 0 |  | ETF2-PSS-2 | 931 |  | -6KA/V | A1TB2-4 | A1TB2-3 | OH_P7S_2PI | pc_oh_pss_7s_2p_i | 18 | 2 | 6
5 | 18 | 15 | pc_oh_pss_4s_2p_v | OH_P4S_2PV | 300 v/v | A | 0 |  | ETF2-PSS-2 | 931 |  | 300V/V | A1TB2-5 | A1TB2-6 | OH_P8S_2PV | pc_oh_pss_8s_2p_v | 18 | 2 | 7
5 | 18 | 16 | pc_oh_pss_3s_2p_v | OH_P3S_2PV | 300 v/v | B | 0 |  | ETF2-PSS-2 | 931 |  | 300V/V | A1TB2-7 | A1TB2-8 | OH_P7S_2PV | pc_oh_pss_7s_2p_v | 18 | 2 | 8
[15 empty] | TF1_P1C_IA | pc_tf1_pss_1c_ia
18 | 2 | 1 | pc_oh_pss_8s_1p_i | OH_P8S_1PI | 6000 a/v | A | ETF2-PSS-1 | [7 empty] | TF1_P1C_IB | pc_tf1_pss_1c_ib
18 | 2 | 2 | pc_oh_pss_7s_1p_i | OH_P7S_1PI | 6000 a/v | B | 0 | [7 empty] | TF1_P1C_VA | pc_tf1_pss_1c_va
18 | 2 | 3 | pc_oh_pss_8s_1p_v | OH_P8S_1PV | 300 v/v | A | 0 | [7 empty] | TF1_P1C_VB | pc_tf1_pss_1c_vb
18 | 2 | 4 | pc_oh_pss_7s_1p_v | OH_P7S_1PV | 300 v/v | B | 0 | [7 empty] | TF1_P2C_IA | pc_tf1_pss_2c_ia
18 | 2 | 5 | pc_oh_pss_8s_2p_i | OH_P8S_2PI | 6000 a/v | A | ETF2-PSS-2 | [7 empty] | TF1_P2C_IB | pc_tf1_pss_2c_ib
18 | 2 | 6 | pc_oh_pss_7s_2p_i | OH_P7S_2PI | 6000 a/v | B | 0 | [7 empty] | TF1_P2C_VA | pc_tf1_pss_2c_va
18 | 2 | 7 | pc_oh_pss_8s_2p_v | OH_P8S_2PV | 300 v/v | A | 0 | [7 empty] | TF1_P2C_VB | pc_tf1_pss_2c_vb
18 | 2 | 8 | pc_oh_pss_7s_2p_v | OH_P7S_2PV | 300 v/v | B | 0 | [7 empty] | TF1_P3C_IA | pc_tf1_pss_3c_ia
[15 empty] | TF1_P3C_IB | pc_tf1_pss_3c_ib
| spare OH PSS | [13 empty] | TF1_P3C_VA | pc_tf1_pss_3c_va
? | ? | ? |  |  |  |  | ETF2-PSS-9 | [7 empty] | TF1_P3C_VB | pc_tf1_pss_3c_vb
[7 empty] | ETF2-PSS-9 | [7 empty] | TF1_P4C_IA | pc_tf1_pss_4c_ia
[7 empty] | ETF2-PSS-9 | [7 empty] | TF1_P4C_IB | pc_tf1_pss_4c_ib
[7 empty] | ETF2-PSS-9 | [7 empty] | TF1_P4C_VA | pc_tf1_pss_4c_va
[7 empty] | ETF2-PSS-A | [7 empty] | TF1_P4C_VB | pc_tf1_pss_4c_vb
[7 empty] | ETF2-PSS-A | [7 empty] | TF1_P5C_IA | pc_tf1_pss_5c_ia
[7 empty] | ETF2-PSS-A | [7 empty] | TF1_P5C_IB | pc_tf1_pss_5c_ib
[7 empty] | ETF2-PSS-A | [7 empty] | TF1_P5C_VA | pc_tf1_pss_5c_va
[15 empty] | TF1_P5C_VB | pc_tf1_pss_5c_vb
[15 empty] | TF1_P8C_VA | pc_tf1_pss_8c_va
19 | 2 | 1 | pc_pf1au_pss_2s_i | PF1AU_P2SI | 6000 a/v | A | EOH1-PSS-1 | [7 empty] | TF1_P8C_VB | pc_tf1_pss_8c_vb
19 | 2 | 2 | pc_pf1au_pss_1s_i | PF1AU_P1SI | 6000 a/v | B | EOH1-PSS-1
19 | 2 | 3 | pc_pf1au_pss_2s_v | PF1AU_P2SV | 300 v/v | A | EOH1-PSS-1
19 | 2 | 4 | pc_pf1au_pss_1s_v | PF1AU_P1SV | 300 v/v | B | EOH1-PSS-1
19 | 2 | 5 | pc_chi_pss_2s_1p_i | CHI_P2S_1PI | 6000 a/v | A | EOH1-PSS-2
19 | 2 | 6 | pc_chi_pss_1s_2p_i | CHI_P1S_2PI | 6000 a/v | B | EOH1-PSS-2
19 | 2 | 7 | pc_chi_pss_2s_1p_v | CHI_P2S_1PV | 300 v/v | A | EOH1-PSS-2
19 | 2 | 8 | pc_chi_pss_1s_2p_v | CHI_P1S_2PV | 300 v/v | B | EOH1-PSS-2
19 | 2 | 9 | pc_pf3u_pss_2s_1p_i | PF3U_P2S_1PI | 6000 a/v | A | EOH2-PSS-1
19 | 2 | 10 | pc_pf3u_pss_1s_1p_i | PF3U_P1S_1PI | 6000 a/v | B | EOH2-PSS-1
19 | 2 | 11 | pc_pf3u_pss_2s_1p_v | PF3U_P2S_1PV | 300 v/v | A | EOH2-PSS-1
19 | 2 | 12 | pc_pf3u_pss_1s_1p_v | PF3U_P1S_1PV | 300 v/v | B | EOH2-PSS-1
10 | 17 | 1 | pc_pf3u_pss_2s_2p_i | PF3U_P2S_2PI | 6000 a/v | A | EEF1-PSS-1
10 | 17 | 2 | pc_pf3u_pss_1s_2p_i | PF3U_P1S_2PI | 6000 a/v | B | EEF1-PSS-1
10 | 17 | 3 | pc_pf3u_pss_2s_2p_v | PF3U_P2S_2PV | 300 v/v | A | EEF1-PSS-1
10 | 17 | 4 | pc_pf3u_pss_1s_2p_v | PF3U_P1S_2PV | 300 v/v | B | EEF1-PSS-1
10 | 17 | 5 | pc_pf3l_pss_2s_2p_i | PF3L_P2S_2PI | 6000 a/v | A | EEF1-PSS-2 |  | OH COIL
10 | 17 | 6 | pc_pf3l_pss_1s_2p_i | PF3L_P1S_2PI | 6000 a/v | B | EEF1-PSS-2 | [7 empty] | TF2_P7C_IB | pc_tf2_pss_7c_ib
10 | 17 | 7 | pc_pf3l_pss_2s_2p_v | PF3L_P2S_2PV | 300 v/v | A | EEF1-PSS-2 | [7 empty] | TF2_P7C_IA | pc_tf2_pss_7c_ia
10 | 17 | 8 | pc_pf3l_pss_1s_2p_v | PF3L_P1S_2PV | 300 v/v | B | EEF1-PSS-2 | [7 empty] | TF2_P7C_VB | pc_tf2_pss_7c_vb
10 | 17 | 9 | pc_pf4_pss_2s_i | PF4_P2SI | 6000 a/v | A | EEF2-PSS-1 | [7 empty] | TF2_P7C_VA | pc_tf2_pss_7c_va
10 | 17 | 10 | pc_pf4_pss_1s_i | PF4_P1SI | 6000 a/v | B | EEF2-PSS-1 | [7 empty] | TF2_P5C_IB | pc_tf2_pss_5c_ib
10 | 17 | 11 | pc_pf4_pss_2s_v | PF4_P2SV | 300 v/v | A | EEF2-PSS-1 | [7 empty] | TF2_P5C_IA | pc_tf2_pss_5c_ia
10 | 17 | 12 | pc_pf4_pss_1s_v | PF4_P1SV | 300 v/v | B | EEF2-PSS-1 | [7 empty] | TF2_P5C_VB | pc_tf2_pss_5c_vb
10 | 17 | 13 | not used |  |  | A | EEF2-PSS-2 | [7 empty] | TF2_P5C_VA | pc_tf2_pss_5c_va
10 | 17 | 14 | not used |  |  | B | EEF2-PSS-2 | [7 empty] | TF2_P2C_IA | pc_tf2_pss_2c_ia
10 | 17 | 15 | not used |  |  | A | EEF2-PSS-2 | [7 empty] | TF2_P2C_IB | pc_tf2_pss_2c_ib
10 | 17 | 16 | not used |  |  | B | EEF2-PSS-2 | [7 empty] | TF2_P2C_VA | pc_tf2_pss_2c_va
[15 empty] | TF2_P2C_VB | pc_tf2_pss_2c_vb
[15 empty] | TF2_P4C_IA | pc_tf2_pss_4c_ia
12 | 17 | 1 | pc_pf1cl_pss_2s_1p_i | PF1CL_P2S1PI | 6000 a/v | A | EEF3-PSS-1 | [7 empty] | TF2_P4C_IB | pc_tf2_pss_4c_ib
12 | 17 | 2 | pc_pf1cl_pss_1s_1p_i | PF1CL_P1S1PI | 6000 a/v | B | EEF3-PSS-1 | [7 empty] | TF2_P4C_VA | pc_tf2_pss_4c_va
12 | 17 | 3 | pc_pf1cl_pss_2s_1p_v | PF1CL_P2S1PV | 300 v/v | A | EEF3-PSS-1 | [7 empty] | TF2_P4C_VB | pc_tf2_pss_4c_vb
12 | 17 | 4 | pc_pf1cl_pss_1s_1p_v | PF1CL_P1S1PV | 300 v/v | B | EEF3-PSS-1 | [7 empty] | TF2_P3C_IB | pc_tf2_pss_3c_ib
12 | 17 | 5 | pc_pf1cl_pss_2s_2p_i | PF1CL_P2S2PI | 6000 a/v | A | EEF3-PSS-2 | [7 empty] | TF2_P3C_IA | pc_tf2_pss_3c_ia
12 | 17 | 6 | pc_pf1cl_pss_1s_2p_i | PF1CL_P1S2PI | 6000 a/v | B | EEF3-PSS-2 | [7 empty] | TF2_P3C_VB | pc_tf2_pss_3c_vb
12 | 17 | 7 | pc_pf1cl_pss_2s_2p_v | PF1CL_P2S2PV | 300 v/v | A | EEF3-PSS-2 | [7 empty] | TF2_P3C_VA | pc_tf2_pss_3c_va
12 | 17 | 8 | pc_pf1cl_pss_1s_2p_v | PF1CL_P1S2PV | 300 v/v | B | EEF3-PSS-2 | [7 empty] | TF2_P1C_IB | pc_tf2_pss_1c_ib
12 | 17 | 9 | former pf1b |  | 6000 a/v |  | EEF4-PS-1, Section A | [7 empty] | TF2_P1C_IA | pc_tf2_pss_1c_ia
12 | 17 | 10 | former pf1b |  | 6000 a/v |  | EEF4-PS-1, Section B | [7 empty] | TF2_P1C_VB | pc_tf2_pss_1c_vb
12 | 17 | 11 | former pf1b |  | 300 v/v |  | EEF4-PS-1, Section A | [7 empty] | TF2_P1C_VA | pc_tf2_pss_1c_va
12 | 17 | 12 | former pf1b |  | 300 v/v |  | EEF4-PS-1, Section B | [7 empty] | TF2_P6C_IA | pc_tf2_pss_6c_ia
12 | 17 | 13 | pc_pf1cu_pss_2s_1p_i | PF1CU_P2S1PI | 6000 a/v | A | EEF4-PSS-2 | [7 empty] | TF2_P6C_IB | pc_tf2_pss_6c_ib
12 | 17 | 14 | pc_pf1cu_pss_1s_1p_i | PF1CU_P1S1PI | 6000 a/v | B | EEF4-PSS-2 | [7 empty] | TF2_P6C_VA | pc_tf2_pss_6c_va
12 | 17 | 15 | pc_pf1cu_pss_2s_1p_v | PF1CU_P2S1PV | 300 v/v | A | EEF4-PSS-2 | [7 empty] | TF2_P6C_VB | pc_tf2_pss_6c_vb
12 | 17 | 16 | pc_pf1cu_pss_1s_1p_v | PF1CU_P1S1PV | 300 v/v | B | EEF4-PSS-2 | [7 empty] | TF2_P8C_IA | pc_tf2_pss_8c_ia
[15 empty] | TF2_P8C_IB | pc_tf2_pss_8c_ib
[15 empty] | TF2_P8C_VA | pc_tf2_pss_8c_va
18 | 2 | 13 | pc_hf_pss_1A_i | HF_P1A_I | 6000 a/v | A | EHF-PSS-1 | [7 empty] | TF2_P8C_VB | pc_tf2_pss_8c_vb
18 | 2 | 14 | pc_hf_pss_1B_i | HF_P1B_I | 6000 a/v | A | EHF-PSS-1
18 | 2 | 15 | pc_hf_pss_1A_v | HF_P1A_V | 300 v/v | A | EHF-PSS-1
18 | 2 | 16 | pc_hf_pss_1B_v | HF_P1B_V | 300 v/v | A | EHF-PSS-1
20 | 2 | 1 | pc_pf2l_pss_2s_i | PF2L_P2SI | 6000 a/v | A | EOH3-PSS-1
20 | 2 | 2 | pc_pf2l_pss_1s_i | PF2L_P1SI | 6000 a/v | B | EOH3-PSS-1
20 | 2 | 3 | pc_pf2l_pss_2s_v | PF2L_P2SV | 300 v/v | A | EOH3-PSS-1
20 | 2 | 4 | pc_pf2l_pss_1s_v | PF2L_P1SV | 300 v/v | B | EOH3-PSS-1
20 | 2 | 5 | pc_pf1cu_pss_2s_2p_i | PF1CU_P2S2PI | 6000 a/v | A | EOH3-PSS-2
20 | 2 | 6 | pc_pf1cu_pss_1s_2p_i | PF1CU_P1S2PI | 6000 a/v | B | EOH3-PSS-2
20 | 2 | 7 | pc_pf1cu_pss_2s_2p_v | PF1CU_P2S2PV | 300 v/v | A | EOH3-PSS-2
20 | 2 | 8 | pc_pf1cu_pss_1s_2p_v | PF1CU_P1S2PV | 300 v/v | B | EOH3-PSS-2
20 | 2 | 9 | pc_pf3l_pss_2s_1p_i | PF3L_P2S_1PI | 6000 a/v | A | EOH4-PSS-1
20 | 2 | 10 | pc_pf3l_pss_1s_1p_i | PF3L_P1S_1PI | 6000 a/v | B | EOH4-PSS-1
20 | 2 | 11 | pc_pf3l_pss_2s_1p_v | PF3L_P2S_1PV | 300 v/v | A | EOH4-PSS-1
20 | 2 | 12 | pc_pf3l_pss_1s_1p_v | PF3L_P1S_1PV | 300 v/v | B | EOH4-PSS-1
21 | 2 | 1 | pc_pf2u_pss_2s_i | PF2U_P2SI | 6000 a/v | A | EOH5-PSS-1
21 | 2 | 2 | pc_pf2u_pss_1s_i | PF2U_P1SI | 6000 a/v | B | EOH5-PSS-1
21 | 2 | 3 | pc_pf2u_pss_2s_v | PF2U_P2SV | 300 v/v | A | EOH5-PSS-1
21 | 2 | 4 | pc_pf2u_pss_1s_v | PF2U_P1SV | 300 v/v | B | EOH5-PSS-1
21 | 2 | 5 | section A not used |  | 6000 a/v | A | EOH5-PSS-2
21 | 2 | 6 | pc_pf5_pss_2s_i | PF5_P2SI | 6000 a/v | B | EOH5-PSS-2
21 | 2 | 7 | section A not used |  | 300 v/v | A | EOH5-PSS-2
21 | 2 | 8 | pc_pf5_pss_2s_v | PF5_P2SV | 300 v/v | B | EOH5-PSS-2
21 | 2 | 9 | pc_pf5_pss_3s_i | PF5_P3SI | 6000 a/v | A | EOH6-PSS-1
21 | 2 | 10 | pc_pf5_pss_1s_i | PF5_P1SI | 6000 a/v | B | EOH6-PSS-1
21 | 2 | 11 | pc_pf5_pss_3s_v | PF5_P3SV | 300 v/v | A | EOH6-PSS-1
21 | 2 | 12 | pc_pf5_pss_1s_v | PF5_P1SV | 300 v/v | B | EOH6-PSS-1
8 | 16 | 1 | pc_tf_pf1_gfc_p | ? | 1v=0ma, 4v=0.100a |  | ? | [7 empty] | TF1_P6C_IB | pc_tf1_pss_6c_ib
8 | 16 | 2 | pc_tf_pf1_gfc_n | ? | 1v=0ma, 4v=0.100a |  | ? | [7 empty] | TF1_P6C_VA | pc_tf1_pss_6c_va
8 | 16 | 3 | pc_oh_gfc_p | ? | 1v=0ma, 4v=0.100a |  | ? | [7 empty] | TF1_P6C_VB | pc_tf1_pss_6c_vb
8 | 16 | 4 | pc_oh_gfc_n | ? | 1v=0ma, 4v=0.100a |  | ? | [7 empty] | TF1_P7C_IA | pc_tf1_pss_7c_ia
8 | 16 | 5 | pc_pf2345_gfc_p | ? | 1v=0ma, 4v=0.100a |  | ? | [7 empty] | TF1_P7C_IB | pc_tf1_pss_7c_ib
8 | 16 | 6 | pc_pf2345_gfc_n | ? | 1v=0ma, 4v=0.100a |  | ? | [7 empty] | TF1_P7C_VA | pc_tf1_pss_7c_va
8 | 16 | 7 | pc_chi_gfc_p | ? | 1v=0ma, 4v=0.100a |  | ? | [7 empty] | TF1_P7C_VB | pc_tf1_pss_7c_vb
8 | 16 | 8 | pc_chi_gfc_n | ? | 1v=0ma, 4v=0.100a |  | ? | [7 empty] | TF1_P8C_IA | pc_tf1_pss_8c_ia
|  |  | epics Pvname & mds tag | mds node |  |  | alternate tag
18 | 16 | 1 | pc_tf_pss_perm | tf_pperm | 1 V/V | volts
18 | 16 | 2 | pc_oh_pss_perm | oh_pperm | 1 V/V | volts
18 | 16 | 3 | pc_pf1_pss_perm | pf1_pperm | 1 V/V | volts
18 | 16 | 4 | pc_pf2_pss_perm | pf2_pperm | 1 V/V | volts
18 | 16 | 5 | pc_tf_lvl1_flt | tf_lvl1_flt | 1 V/V | volts | pc_tf_lvl_1_flt
18 | 16 | 6 | pc_oh_lvl1_flt | oh_lvl1_flt | 1 V/V | volts | pc_oh_lvl_1_flt
18 | 16 | 7 | pc_pf1_lvl1_flt | pf1_lvl1_flt | 1 V/V | volts | pc_pf1_lvl_1_flt
18 | 16 | 8 | pc_pf2_lvl1_flt | pf2_lvl1_flt | 1 V/V | volts | pc_pf2_lvl_1_flt
18 | 16 | 9 | pc_paux_flt | paux_flt | 1 V/V | volts
18 | 16 | 10 | Spare (0-5V) |  | 1 V/V | volts
18 | 16 | 11 | Spare (0-5V) |  | 1 V/V | volts
18 | 16 | 12 | Spare (0-5V) |  | 1 V/V | volts
18 | 16 | 13 | Spare (0-5V) |  | 1 V/V | volts
18 | 16 | 14 | Spare (0-5V) |  | 1 V/V | volts
18 | 16 | 15 | Spare (0-5V) |  | 1 V/V | volts
18 | 16 | 16 | Spare (0-5V) |  | 1 V/V | volts
(tag)
38 | 10 | 1 | pc_RWM1_I | PC_RWM1_I | 500 A/V | amps | test cell crate
38 | 10 | 2 | pc_RWM2_I | PC_RWM2_I | 500 A/V | amps | shared with FISO
38 | 10 | 3 | pc_RWM3_I | PC_RWM3_I | 500 A/V | amps
38 | 10 | 4 | pc_RWM4_I | PC_RWM4_I | 500 A/V | amps
38 | 10 | 5 | pc_RWM5_I | PC_RWM5_I | 500 A/V | amps
38 | 10 | 6 | pc_RWM6_I | PC_RWM6_I | 500 A/V | amps
(tag)
37 | 8 | 1 | same as tag but all lowercase | PC_SPA2_FLTSTATUS | 1
37 | 8 | 2 | same as tag but all lowercase | PC_SPA2_SU4_CHRG_I | 125A/V | TD chan 2 | +5V => 625 amps
37 | 8 | 3 | same as tag but all lowercase | PC_SPA2_SU5_CHRG_I | 125A/V | TD chan 3 | +5V => 625 amps
37 | 8 | 4 | same as tag but all lowercase | PC_SPA2_SU6_CHRG_I | 125A/V | TD chan 4 | +5V => 625 amps
37 | 8 | 5 | same as tag but all lowercase | PC_SPA2_SU4_FLT | 1
37 | 8 | 6 | same as tag but all lowercase | PC_SPA2_SU5_FLT | 1
37 | 8 | 7 | same as tag but all lowercase | PC_SPA2_SU6_FLT | 1
37 | 8 | 8 | same as tag but all lowercase | PC_SPA2_SU4_PERM | 1
37 | 8 | 9 | same as tag but all lowercase | PC_SPA2_SU5_PERM | 1
37 | 8 | 10 | same as tag but all lowercase | PC_SPA2_SU6_PERM | 1
37 | 8 | 11 | same as tag but all lowercase | PC_SPA2_SU4_REF | 2 | TD chan 11 | the voltage request to get a set current
37 | 8 | 12 | same as tag but all lowercase | PC_SPA2_SU5_REF | 2 | TD chan 12
37 | 8 | 13 | same as tag but all lowercase | PC_SPA2_SU6_REF | 2 | TD chan 13
37 | 8 | 14 | same as tag but all lowercase | PC_SPA2_CHAN14 | 1
37 | 8 | 15 | same as tag but all lowercase | PC_SPA2_CHAN15 | 1
37 | 8 | 16 | same as tag but all lowercase | PC_SPA2_CHAN16 | 1
full path \ENGINEERING::TOP.EPICS.FCPC.DIGITIZERS:
|  |  | no EPICS name, just MDS tag | MDS node | Scaling
nstx-dtacq209 |  | 1 | PC_PCUR_1_LG | not shown here. Look in skylark directory | 1000000 | amps
nstx-dtacq209 |  | 2 | PC_PF1AU_CHI_CUR_1 | /u/nstx/fcpc/config/DT209 | 5000 | amps
nstx-dtacq209 |  | 3 | PC_PF1BU_CUR_1 |  | 1 | amps
nstx-dtacq209 |  | 4 | PC_PF1CU_CUR_1 |  | 2500 | amps
nstx-dtacq209 |  | 5 | PC_PF2U_CUR_1 |  | 5000 | amps
nstx-dtacq209 |  | 6 | PC_PF3U_CUR_1 |  | 5000 | amps
nstx-dtacq209 |  | 7 | PC_PF4_CUR_1 |  | 3000 | amps
nstx-dtacq209 |  | 8 | PC_PF5_CUR_1 |  | 5000 | amps
nstx-dtacq209 |  | 9 | PC_PF3L_CUR_1 |  | 2500 | amps
nstx-dtacq209 |  | 10 | PC_PF2L_CUR_1 |  | 5000 | amps
nstx-dtacq209 |  | 11 | PC_PF1CL_CUR_1 |  | 5000 | amps
nstx-dtacq209 |  | 12 | PC_PF1BL_CUR_1 |  | 1 | amps
nstx-dtacq209 |  | 13 | PC_PF1AL_CUR_1 |  | 2500 | amps
nstx-dtacq209 |  | 14 | PC_OH_CUR_1 |  | 2500 | amps
nstx-dtacq209 |  | 15 | PC_TF_CUR_1 |  | 15000 | amps
nstx-dtacq209 |  | 16 | PC_DUMMY_LOAD_CUR |  | 2500 | amps
nstx-dtacq209 |  | 17 | PC_PCUR_2_LG |  | 1000000 | amps
nstx-dtacq209 |  | 18 | PC_PF1AU_CHI_CUR_2 |  | 5000 | amps
nstx-dtacq209 |  | 19 | PC_PF1BU_CUR_2 |  | 1 | amps
nstx-dtacq209 |  | 20 | PC_PF1CU_CUR_2 |  | 2500 | amps
nstx-dtacq209 |  | 21 | PC_PF2U_CUR_2 |  | 2500 | amps
nstx-dtacq209 |  | 22 | PC_PF3U_CUR_2 |  | 2500 | amps
nstx-dtacq209 |  | 23 | PC_PF4_CUR_2 |  | 3000 | amps
nstx-dtacq209 |  | 24 | PC_PF5_CUR_2 |  | 2500 | amps
nstx-dtacq209 |  | 25 | PC_PF3L_CUR_2 |  | 2500 | amps
nstx-dtacq209 |  | 26 | PC_PF2L_CUR_2 |  | 2500 | amps
nstx-dtacq209 |  | 27 | PC_PF1CL_CUR_2 |  | 5000 | amps
nstx-dtacq209 |  | 28 | PC_PF1BL_CUR_2 |  | 1 | amps
nstx-dtacq209 |  | 29 | PC_PF1AL_CUR_2 |  | 2500 | amps
nstx-dtacq209 |  | 30 | PC_OH_CUR_2 |  | 2500 | amps
nstx-dtacq209 |  | 31 | PC_TF_CUR_2 |  | 15000 | amps
nstx-dtacq209 |  | 32 | PC_ENG_SPARE |  | 1 | amps
nstx-dtacq209 |  | 33 | PC_TF_BR_1_CUR_3 |  | 2500 | amps
nstx-dtacq209 |  | 34 | PC_TF_BR_2_CUR_3 |  | 2500 | amps
nstx-dtacq209 |  | 35 | PC_TF_BR_3_CUR_3 |  | 2500 | amps
nstx-dtacq209 |  | 36 | PC_TF_BR_4_CUR_3 |  | 2500 | amps
nstx-dtacq209 |  | 37 | PC_TF_BR_5_CUR_3 |  | 2500 | amps
nstx-dtacq209 |  | 38 | PC_TF_BR_6_CUR_3 |  | 2500 | amps
nstx-dtacq209 |  | 39 | PC_TF_BR_7_CUR_3 |  | 2500 | amps
nstx-dtacq209 |  | 40 | PC_TF_BR_8_CUR_3 |  | 2500 | amps
nstx-dtacq209 |  | 41 | PC_OH_BR_1_CUR_1 |  | 1 | amps
nstx-dtacq209 |  | 42 | PC_OH_BR_2_CUR_1 |  | 1 | amps
nstx-dtacq209 |  | 43 | PC_OH_BR_1_CUR_2 |  | 1 | amps
nstx-dtacq209 |  | 44 | PC_OH_BR_2_CUR_2 |  | 1 | amps
nstx-dtacq209 |  | 45 | PC_HSC3_CHAN_13 |  | 1 | amps
nstx-dtacq209 |  | 46 | PC_NBP |  | 1 | watts
nstx-dtacq209 |  | 47 | PC_PCUR_1_HG |  | 10000 | amps
nstx-dtacq209 |  | 48 | PC_PCUR_2_HG |  | 10000 | amps
nstx-dtacq209 |  | 49 | PC_TF_LKAT_CUR_1 |  | 1 | amps
nstx-dtacq209 |  | 50 | PC_FO_CHAN_16 |  | 1 | volts
nstx-dtacq209 |  | 51 | PC_FO_CHAN_15 |  | 1 | volts
nstx-dtacq209 |  | 52 | PC_FO_CHAN_14 |  | 1 | volts
nstx-dtacq209 |  | 53 | PC_FO_CHAN_13 |  | 1 | volts
nstx-dtacq209 |  | 54 | PC_FO_CHAN_12 |  | 1 | volts
nstx-dtacq209 |  | 55 | PC_FO_CHAN_11 |  | 1 | volts
nstx-dtacq209 |  | 56 | PC_ROG_1_HG |  | 10000 | amps
nstx-dtacq209 |  | 57 | PC_ROG_1_LG |  | 80000 | amps
nstx-dtacq209 |  | 58 | PC_IVV_IT_1 |  | 60000 | amps
nstx-dtacq209 |  | 59 | PC_IVV_IT_2 |  | 60000 | amps
nstx-dtacq209 |  | 60 | PC_IVV_U_E_S |  | 120000 | amps
nstx-dtacq209 |  | 61 | PC_IVV_L_E_S |  | 120000 | amps
nstx-dtacq209 |  | 62 | PC_IVV_U_O_S |  | 120000 | amps
nstx-dtacq209 |  | 63 | PC_IVV_L_O_S |  | 120000 | amps
nstx-dtacq209 |  | 64 | PC_ROG_2_HG |  | 100000 | amps
nstx-dtacq209 |  | 65 | PC_ROG_2_LG |  | 800000 | amps
nstx-dtacq209 |  | 66 | PC_IVV_In_1 |  | 150000 | amps
nstx-dtacq209 |  | 67 | PC_IVV_Out_1 |  | 250000 | amps
nstx-dtacq209 |  | 68 | PC_IVV_Tot_1 |  | 400000 | amps
nstx-dtacq209 |  | 69 | PC_IPCALC_TELEM_1 |  | 1 | volts
nstx-dtacq209 |  | 70 | PC_IPCALC_SPARE_1 |  | 1 | volts
nstx-dtacq209 |  | 71 | PC_NB_PERM_1 |  | 1 | volts
nstx-dtacq209 |  | 72 | PC_CHI_PERM |  | 1 | volts
nstx-dtacq209 |  | 73 | PC_RF_PERM |  | 1 | volts
nstx-dtacq209 |  | 74 | PC_GIS_PERM |  | 1 | volts
nstx-dtacq209 |  | 75 | PC_IVV_In_2 |  | 150000 | amps
nstx-dtacq209 |  | 76 | PC_IVV_Out_2 |  | 250000 | amps
nstx-dtacq209 |  | 77 | PC_IVV_Tot_2 |  | 400000 | amps
nstx-dtacq209 |  | 78 | PC_IPCALC_TELEM_2 |  | 1 | volts
nstx-dtacq209 |  | 79 | PC_IPCALC_SPARE_2 |  | 1 | volts
nstx-dtacq209 |  | 80 | PC_NB_PERM_2 |  | 1 | volts
nstx-dtacq209 |  | 81 | PC_SOP_EOP_GATE |  | 1 | volts
nstx-dtacq209 |  | 82 | PC_TF_LKAT_CUR_2 |  | 1 | amps
nstx-dtacq209 |  | 83 | PC_TF_HCS_FLT |  | 1 | volts
nstx-dtacq209 |  | 84 | PC_OHPFCHI_HCS_FLT |  | 1 | volts
nstx-dtacq209 |  | 85 | PC_TF_BR_12_CUR_1 |  | 3750 | amps
nstx-dtacq209 |  | 86 | PC_TF_BR_34_CUR_1 |  | 3750 | amps
nstx-dtacq209 |  | 87 | PC_TF_BR_56_CUR_1 |  | 3750 | amps
nstx-dtacq209 |  | 88 | PC_TF_BR_78_CUR_1 |  | 3750 | amps
nstx-dtacq209 |  | 89 | PC_TF_BR_12_CUR_2 |  | 3750 | amps
nstx-dtacq209 |  | 90 | PC_TF_BR_34_CUR_2 |  | 3750 | amps
nstx-dtacq209 |  | 91 | PC_TF_BR_56_CUR_2 |  | 3750 | amps
nstx-dtacq209 |  | 92 | PC_TF_BR_78_CUR_2 |  | 3750 | amps
nstx-dtacq209 |  | 93 | PC_DITFDT |  | 50 | kA/sec
nstx-dtacq209 |  | 94 | PC_DM_VTF |  | 222.72 | volts
nstx-dtacq209 |  | 95 | PC_DM_ITF |  | 20000 | amps
nstx-dtacq209 |  | 96 | PC_DM_FLUX |  | 4.036 | webers
full path \ENGINEERING::TOP.EPICS.FCPC.DIGITIZERS:
|  |  | no EPICS name, just MDS tag | MDS node | Scaling
nstx-dtacq214 |  | 1 | PC_PF1AU_SDS_VD1_1 | not shown here. Look in skylark directory | 3168 | volts
nstx-dtacq214 |  | 2 | PC_PF1AU_SDS_VD2_1 | /u/nstx/fcpc/config/DT214 | 3168 | volts
nstx-dtacq214 |  | 3 | PC_PF3U_SDS_VD1_1 |  | 3168 | volts
nstx-dtacq214 |  | 4 | PC_PF3U_SDS_VD2_1 |  | 3168 | volts
nstx-dtacq214 |  | 5 | PC_PF2L_SDS_VD1_1 |  | 3168 | volts
nstx-dtacq214 |  | 6 | PC_PF2L_SDS_VD2_1 |  | 3168 | volts
nstx-dtacq214 |  | 7 | PC_PF3L_SDS_VD1_1 |  | 3168 | volts
nstx-dtacq214 |  | 8 | PC_PF3L_SDS_VD2_1 |  | 3168 | volts
nstx-dtacq214 |  | 9 | PC_PF2U_SDS_VD1_1 |  | 3168 | volts
nstx-dtacq214 |  | 10 | PC_PF2U_SDS_VD2_1 |  | 3168 | volts
nstx-dtacq214 |  | 11 | PC_PF5_SDS_VD1_1 |  | 3168 | volts
nstx-dtacq214 |  | 12 | PC_PF5_SDS_VD2_1 |  | 3168 | volts
nstx-dtacq214 |  | 13 | PC_PF1AL_SDS_VD1_1 |  | 3168 | volts
nstx-dtacq214 |  | 14 | PC_PF1AL_SDS_VD2_1 |  | 3168 | volts
nstx-dtacq214 |  | 15 | PC_PF4_SDS_VD1_1 |  | 3168 | volts
nstx-dtacq214 |  | 16 | PC_PF4_SDS_VD2_1 |  | 3168 | volts
nstx-dtacq214 |  | 17 | PC_PF1CL_SDS_VD1_1 |  | 3168 | volts
nstx-dtacq214 |  | 18 | PC_PF1CL_SDS_VD2_1 |  | 3168 | volts
nstx-dtacq214 |  | 19 | PC_PF1CU_SDS_VD1_1 |  | 3168 | volts
nstx-dtacq214 |  | 20 | PC_PF1CU_SDS_VD2_1 |  | 3168 | volts
nstx-dtacq214 |  | 21 | PC_SPARE2_SDS_VD1_1 |  | 3168 | volts
nstx-dtacq214 |  | 22 | PC_SPARE2_SDS_VD2_1 |  | 3168 | volts
nstx-dtacq214 |  | 23 | PC_HF_SDS_VD1_1 |  | 3168 | volts
nstx-dtacq214 |  | 24 | PC_HF_SDS_VD2_1 |  | 3168 | volts
nstx-dtacq214 |  | 25 | PC_RWM_SDS_VD1_1 |  | 3168 | volts
nstx-dtacq214 |  | 26 | PC_RWM_SDS_VD2_1 |  | 3168 | volts
nstx-dtacq214 |  | 27 | PC_TF_SDS_VD1_1 |  | 3168 | volts
nstx-dtacq214 |  | 28 | PC_TF_SDS_VD2_1 |  | 3168 | volts
nstx-dtacq214 |  | 29 | PC_OH_SDS_VD1_1 |  | 3168 | volts
nstx-dtacq214 |  | 30 | PC_OH_SDS_VD2_1 |  | 3168 | volts
nstx-dtacq214 |  | 31 | PC_TF_GNDCUR |  | 0.02 | amps
nstx-dtacq214 |  | 32 | PC_OH_GNDCUR |  | 0.02 | amps
nstx-dtacq214 |  | 33 | PC_CHI_GNDCUR |  | 0.02 | amps
nstx-dtacq214 |  | 34 | PC_PF_GNDCUR |  | 0.02 | amps
nstx-dtacq214 |  | 35 | PC_SP1_GNDCUR |  | 0.02 | amps
nstx-dtacq214 |  | 36 | PC_SP2_GNDCUR |  | 0.02 | amps
nstx-dtacq214 |  | 37 | PC_SP3_GNDCUR |  | 0.02 | amps
nstx-dtacq214 |  | 38 | PC_SP4_GNDCUR |  | 0.02 | amps
|  |  | raw dtacq head node: pc_dt196_01 | full path \ENGINEERING::TOP.EPICS.FCPC.DIGITIZERS: |  |  |  | from tree | from TCL script
|  |  | no EPICS name, just MDS tag | MDS node | Scaling (units/volt) | units |  |  | Scaling
spa-dtacq1 |  | 1 | PC_SPA_SU1_I1 | not shown here. Look in skylark directory | 800A/V (+/-5V => +/- 4,000 amps) | amps | Sub Unit 1 Output Current 1 |  | 400 | amps
spa-dtacq1 |  | 2 | PC_SPA_SU1_I2 | /u/nstx/fcpc/config/ | 800A/V (+/-5V => +/- 4,000 amps) | amps | Sub Unit 1 Output Current 2 |  | 400 | amps
spa-dtacq1 |  | 3 | PC_SPA_SU2_I1 |  | 800A/V (+/-5V => +/- 4,000 amps) | amps | Sub Unit 2 Output Current 1 |  | 400 | amps
spa-dtacq1 |  | 4 | PC_SPA_SU2_I2 |  | 800A/V (+/-5V => +/- 4,000 amps) | amps | Sub Unit 2 Output Current 2 |  | 400 | amps
spa-dtacq1 |  | 5 | PC_SPA_SU3_I1 |  | 800A/V (+/-5V => +/- 4,000 amps) | amps | Sub Unit 3 Output Current 1 |  | 400 | amps
spa-dtacq1 |  | 6 | PC_SPA_SU3_I2 |  | 800A/V (+/-5V => +/- 4,000 amps) | amps | Sub Unit 3 Output Current 1 |  | 400 | amps
spa-dtacq1 |  | 7 | PC_SPA1_IDC |  | 400A/V (+/-5V => +/- 2,000 amps) | amps | SPA 1 Total Chrg. Crnt. (SU1&SU2&SU3) |  | 200 | amps
spa-dtacq1 |  | 8 | PC_SPA_SU1_V |  | 200V/V (+/-5V => +/-1,000 volts) | volts | Sub Unit 1 Output Voltage |  | 100 | volts
spa-dtacq1 |  | 9 | PC_SPA_SU2_V |  | 200V/V (+/-5V => +/-1,000 volts) | volts | Sub Unit 2 Output Voltage |  | 100 | volts
spa-dtacq1 |  | 10 | PC_SPA_SU3_V |  | 200V/V (+/-5V => +/-1,000 volts) | volts | Sub Unit 3 Output Voltage |  | 100 | volts
spa-dtacq1 |  | 11 | PC_SPA1_VDC |  | 240 V/V (+5V => 1,200 volts) | volts | SPA 1 VDC |  | 120 | volts
spa-dtacq1 |  | 12 | PC_SPA1_ACP_FLT |  | (1-3V no fault, 6-8V fault) | volts | ACP/SPA 1 Fault Status |  | 1 | volts
spa-dtacq1 |  | 13 | PC_SPA_SU23_CHRG_I |  | 400A/V (+/-5V => +/- 2,000 amps) | amps | sub Unit 2 & 3 Chrg. Crnt.
spa-dtacq1 |  | 14 | PC_SPA_SU3_CHRG_I |  | 400A/V (+/-5V => +/- 2,000 amps) | amps | Sub Unit 3 Chrg. Crnt.
computed in MDS |  |  | PC_SPA_SU2_CHRG_I |  | scaled in digitized signal | amps | su23 - su3
computed in MDS |  |  | PC_SPA_SU1_CHRG_I |  | scaled in digitized signal | amps | Total – su23
spa-dtacq1 |  | 15 | PC_SPA_SU1_FLT |  | 1 | volts | Sub Unit 1 Fault
spa-dtacq1 |  | 16 | PC_SPA_SU2_FLT |  | 1 | volts | Sub Unit 2 Fault
spa-dtacq1 |  | 17 | PC_SPA_SU3_FLT |  | 1 | volts | Sub Unit 3 Fault
spa-dtacq1 |  | 18 | PC_SPA_SU1_PRM |  | 1 | volts | SubUnit1Permissive (Enable)
spa-dtacq1 |  | 19 | PC_SPA_SU2_PRM |  | 1 | volts | SubUnit2Permissive (Enable)
spa-dtacq1 |  | 20 | PC_SPA_SU3_PRM |  | 1 | volts | SubUnit3Permissive (Enable)
spa-dtacq1 |  | 21 | PC_SPA_SU1_REF |  | 1 | volts | Sub Unit 1 Reference. the voltage request to get a set current
spa-dtacq1 |  | 22 | PC_SPA_SU2_REF |  | 1 | volts | Sub Unit 2 Reference
spa-dtacq1 |  | 23 | PC_SPA_SU3_REF |  | 1 | volts | Sub Unit 3 Reference
spa-dtacq1 |  | 24 | PC_SPA_SU4_I1 |  | 400A/V (+/-10V => 4,000 amps) | amps | Sub Unit 4 Output Current 1 |  | 400 | amps
spa-dtacq1 |  | 25 | PC_SPA_SU4_I2 |  | 400A/V (+/-10V => 4,000 amps) | amps | Sub Unit 4 Output Current 2 |  | 400 | amps
spa-dtacq1 |  | 26 | PC_SPA_SU5_I1 |  | 400A/V (+/-10V => 4,000 amps) | amps | Sub Unit 5 Output Current 1 |  | 400 | amps
spa-dtacq1 |  | 27 | PC_SPA_SU5_I2 |  | 400A/V (+/-10V => 4,000 amps) | amps | Sub Unit 5 Output Current 2 |  | 400 | amps
spa-dtacq1 |  | 28 | PC_SPA_SU6_I1 |  | 400A/V (+/-10V => 4,000 amps) | amps | Sub Unit 6 Output Current 1 |  | 400 | amps
spa-dtacq1 |  | 29 | PC_SPA_SU6_I2 |  | 400A/V (+/-10V => 4,000 amps) | amps | Sub Unit 6 Output Current 2 |  | 400 | amps
spa-dtacq1 |  | 30 | PC_SPA2_IDC |  | 200A/V (+10V => 2,000 amps) | amps | SPA 2 Total Chrg. Crnt. |  | 200 | amps
spa-dtacq1 |  | 31 | PC_SPA_SU4_V |  | 100V/V (+/-10V => +/-1,000 volts) | volts | Sub Unit 4 Output Voltage |  | 100 | volts
spa-dtacq1 |  | 32 | PC_SPA_SU5_V |  | 100V/V (+/-10V => +/-1,000 volts) | volts | Sub Unit 5 Output Voltage |  | 100 | volts
spa-dtacq1 |  | 33 | PC_SPA_SU6_V |  | 100V/V (+/-10V => +/-1,000 volts) | volts | Sub Unit 6 Output Voltage |  | 100 | volts
spa-dtacq1 |  | 34 | PC_SPA2_VDC |  | 120V/V (+10V => 1,200 V) | volts | SPA 2 VDC |  | 120 | volts
spa-dtacq1 |  | 35 | PC_SPA_H910_REF |  | 1 | volts | CAMAC Triangle |  | 1 | volts
spa-dtacq1 |  | 36 | PC_SPA2_ACP_FLT |  | (1-3V no fault, 6-8V fault) | volts | ACP/SPA 2 Fault Status |  | 1 | volts

## Revision History
Revision History
Rev 9 By R. Marsala on 04JAN01
Attached is the rev 9 of fcpc_dignames file. Pages 2 and 3 and the header
have been changed (changes have light yellow fill). The changes include:
1. Update of Plasma Current transfer function
2. Addition of Diamagnetic signals
3. Addition of PF1A branch currents
4. Replacing MG signals with 4 magnetic signals
5. Changed header to give a fixed date.
Rev 10 By P. Sichta n 22MAR01
Change Names and Transfer Functions of the following TD signals all in Crate 22, Slot 09.
Channel 3 from pc_chi_gndcur_1,聽 CHI_GNDC_1,聽 200ma/V to pc_TF_gndcur_1,聽 TF_GNDC_1, 20ma/V
Channel 4 from pc_chi_gndcur_1c,聽 CHI_GNDC_1c,聽 100ma/V to pc_TF_gndcur_2,聽 TF_GNDC_2, 10ma/V
Channel 5 from pc_chi_gndcur_2,聽 CHI_GNDC_2,聽 200ma/V to pc_OH_gndcur_1,聽 OH_GNDC_1, 20ma/V
Channel 6 from pc_chi_gndcur_2c,聽 CHI_GNDC_2c,聽 100ma/V to pc_OH_gndcur_2,聽 OH_GNDC_2, 10ma/V
Changed units column to show scaling in amps/volt not kiloamps/volt.
Rev 11 By P. Sichta n 24APR01
Corrections for PF1A addition per CLN.
Rev 12 By P. Sichta 01JUN01
Changed EPICS crate #16 to DAS Crate 42(Note this was actually done in Jan, 2001).
Added signal pc_d(Itf)dt in crate 42.
Rev 13 by RJM 10AUG01
Added /or changed names of the following TD signals all in Crate 22, Slot 9
Channel 1 from unused to pc_TF_gndcur,聽 TF_GNDCUR, 20mA/V
Channel 2 from unused to pc_OH_ gndcur,聽 OH_GNDCUR, 20mA/V
Channel 3 from pc_TF_gndcur_1,聽 TF_GNDCUR_1 to pc_CHI_ gndcur,聽 TF_GNDCUR, 20mA/V
Channel 4 from pc_TF_gndcur_2,聽 TF_GNDCUR_2, 10ma/V to pc_PF1_ gndcur,聽 PF1_GNDCUR, 20mA/V
Channel 5 from pc_OH_gndcur_1,聽 OH_GNDCUR_1, 20ma/V to pc_PF2_ gndcur,聽 PF2_GNDCUR, 20mA/V
Channel 6 from pc_OH_gndcur_2,聽 OH_GNDCUR_2, 10ma/V to pc_SP1_ gndcur,聽 SP1_GNDCUR, 20mA/V
Channel 10 from unused to pc_SP2_ gndcur,聽 SP2_GNDCUR, 20mA/V
Channel 11 from unused to pc_SP3_ gndcur,聽 SP3_GNDCUR, 20mA/V
Rev 14 by PS 16NOV01
Changed crate 22 slot 9 MDSplus node names from GNDCUR to GNDC. Rev 11 used GNDC.
Rev 15 by PS 20NOV01
Corrected PF and SP_GNDCUR names. Only one PF and four spares inst gnd currents.
Rev 16 by PS 07FEB02
Name changes for signal: pc_pf1al_br_1_cur_1f -> pc_pf1al_cur_3_invf
Rev 17 by PS 11FEB02
Changed names of Fast PF1A Branch currents from 13 to 12 chars to match actual shot tree names.
Rev 18 by RJM 06JAN2004
Separated PF4/5 into PF4 and PF5.
Rev 18.1 and 18.2 by RJM 09JAN2004
Added some missing PF4 channels.
Rev 19 by PS 14July2004
1) Changed PF4Cur2 scale factor from 6ka/v to 1ka/v.
2) Changed all PF4 references to RWM. In MDSplus duplicate tags will be used for the RWM signals (i.e. PF4 will also be used until applications are migrated to use RWM tag). In the far future there may be a new PF4 power supply section(s) at which time the PF4 tags will be separated from RWM.
Rev 20 by RJM 07MAR2005
Separated RWM and PF4 power supply sections, and renamed EPICS and MDSplus names, as appropriate.
Rev 21 by PS 24MAR2005
Added SDS signals for RWM (per Corl).
Rev 22 by RJM 28MAR2005 (color changes by PS 29MAR2005)
Added SDS Fast signals for RWM crt 22, slt 19, Chan 9 and 10
Rev 23 by ps 28APR2005
Added SPA digitizer in crate 16.
Rev 24 by RJM 11 May2005
Added SPA Scale Factors for crate 16
Rev 25 by PS on 03March 2006
Documented use of channel 25 (C=42, Slot=8) for Fast/Slow monitoring
Rev 26 by PS on 21MAY2008
Corrected PF1U PSS MDS node names
Rev 27 by PS on 28JAN2010
At RJM's request, removed 908's C=17, N=4 and 9
Sichta req that N=17 also be removed.
These 908's were 'fast' digitizers that nobody looks at (as far as we know). The sigs are also 'slow' dig'd.
Rev 28 by PS on 14FEB2012
908 in C17 N17 reassigned to PF4/5 weld stress signals (circa March 2010)
Rev 29 by PS 15FEB2013
PF4/5 weld stress signals removed from 908 C17 N17. Digitizer no longer needed.
Rev 30 by jd 13Nov2014
Crates 1 & 4 Removed
Rev 31 20FEB2015 PS
Added crate 2 for TF and D-Tacqs to replace crates 22 and 42.
Rev 33 04MAY2015
Changed PF2U CUR2 from 5000 to 2500
Rev 34 08SEP2015
Sichta Added SPA D-Tacq spa-dtacq1 and SPA CAMAC C37. Mozulay corrected SPA scaling factors.
R35 22SEP2015
Sichta made SPA1 charging current naming and scaling corrections.
R36 19OCT2015
Sichta made SPA2 su4-5-6_ref scaling corrections (from 1 to 2).
R37 09NOV015
Sichta added test cell RWM digitizer.
R38 12FEB2016
Sichta added 908c18n16 for hcs plc