## Sheet1
POWER BALANCE IN SPA CIRCUIT
| Load current | Resistance | Power | 3* Pwr. | Loss in SPA per Mfr. | Charging Voltage |  | time | Energy | Volt drop
| 3333 | 0.01595 | 177.1868 | 531.5603 | 78 | 1012 | 900 | 0.005 | 2.6578 | 53.1613
| 525.2573 | 0.16 | 44.1432 | 653.7036 | [5 empty] | 84.0412
| 645.9521 | 0.16 | 66.7607 | 676.321 |  | 945.2393
| 668.3014 | 0.16 | 71.4603 | 681.0206
| 672.9453 | 0.16 | 72.4569 | 682.0172
| 673.93 | 0.16 | 72.6691 | 682.2294
| 674.1397 | 0.16 | 72.7143 | 682.2746
| 674.1844 | 0.16 | 72.7239 | 682.2843
| 674.194 | 0.16 | 72.726 | 682.2863
| 1012 | 927.9588 |  |  | 13.1301
After 1.25 milliseconds the P13 current goes up to 680 Amps
POWER BALANCE IN SPA CIRCUIT if only 1-500mcm wire is used in each pole
| Load current | Resistance | Power | 3* Pwr. | Loss in SPA per Mfr. | Charging Voltage |  | time | Energy | Volt drop
| 3333 | 0.01595 | 177.1868 | 531.5603 | 78 | 1012 | 900 | 0.005 | 2.6578 | 53.1613
| 525.2573 | 0.24 | 66.2148 | 675.7752 | [5 empty] | 126.0617
| 667.762 | 0.24 | 107.0175 | 716.5778 |  | 904.9825
| 708.0808 | 0.24 | 120.3308 | 729.8912
| 721.2363 | 0.24 | 124.8436 | 734.404
| 725.6956 | 0.24 | 126.3922 | 735.9525
| 727.2258 | 0.24 | 126.9258 | 736.4861
| 727.7531 | 0.24 | 127.1099 | 736.6702
| 727.935 | 0.24 | 127.1735 | 736.7338
| 727.9978 | 0.24 | 127.1954 | 736.7557
| 728.0195 | 0.24 | 127.203 | 736.7633
POWER BALANCE IN SPA CIRCUIT if only 1-500mcm wire is used in each pole
| Load current | Resistance | Power | 3* Pwr. | Loss in SPA per Mfr. | Charging Voltage |  | time | Energy | Volt drop
| 3333 | 0.01595 | 177.1868 | 531.5603 | 78 | 1012 | 900 | 0.005 | 2.6578 | 53.1613
| 525.2573 | 0.32 | 88.2865 | 697.8468 | [5 empty] | 168.0823
| 689.5719 | 0.32 | 152.163 | 761.7234 |  | 859.837
| 752.6911 | 0.32 | 181.294 | 790.8544
| 781.4766 | 0.32 | 195.4258 | 804.9862
| 795.4409 | 0.32 | 202.4724 | 812.0327
| 802.4039 | 0.32 | 206.0326 | 815.593
| 805.9219 | 0.32 | 207.8432 | 817.4036
| 807.711 | 0.32 | 208.7671 | 818.3274
| 808.6239 | 0.32 | 209.2393 | 818.7996
| 809.0905 | 0.32 | 209.4808 | 819.0411
| 20 | 0.00397 | 50 | 14.4 | 16.115 | 11.91
| F | dv/dt
| 0.072 | 5060 | 364.32
| iR | L*di.dt | (1/C)* Integ. i*dt
|  |  |  | a | [9 empty] | g | w
| R | L | C | R/2L | 1/LC | (-R/2L)(+/-)((R/2L)^2 - 1/LC) |  | R^2/(4L^2) | l1 | l2 | g | e^l1*.2 | e^l2t | ((R/2L)^2 - 1/LC)^0.5 |  | Cosh(gt) | Sinh(gt)
| 0.1291 | 0.0003 | 0.072 | 215.1683 | 46296.2963 | -214.1122 |  | 46297.4117 | -214.1122 | -216.2244 | 1.0561 | 2.5261e-19 | 1.6557e-19 | 1.0561 | 1.0561 | 1.0224 | 0.2128
| i= A*e^l1t+B*e^l2t | [10 empty] | 8.7038e-20 |  | 1= e^(-at)*(Acoshlt+Bsinhlt)
| At t=0, i=0 |  | A1=A2 | L/C | 2*(L/C)^.5 | [10 empty] | 1.6115 | 1.2637
| At t=200ms, v=1012 |  |  | 0.0041667 | 0.1291 | [8 empty] | (di/dt) at t=.2 is 1012
| A+B=0; B=-A | [12 empty] | 3373333.3333 | Amps/Sec
| i= A*(e^l1t-e^l2t | [10 empty] | a
[12 empty] | (-R/2L) |  |  |  | 1.2983e+68 | 9.6181e+67
e^(at)
|  |  |  | 2.0451e-19 | [12 empty] | 0
|  |  | 0.072 |  |  |  | f | L | C | 2*PI*f*L | 1/(2*PI*f*C)
[7 empty] | 720 | 0.0003 | 0.072 | 1.3572 | 0.0030701
| 1012 | 0.1 | 728.64 |  |  |  | 360 | 0.0003 | 0.072 | 0.67858 | 0.0061402
[7 empty] | 180 | 0.0003 | 0.072 | 0.33929 | 0.01228
| Time constant | 215.1683 |  |  |  |  | 60 | 0.0003 | 0.072 | 0.1131 | 0.036841
|  | 0.0046475 |  |  |  |  | 40 | 0.0003 | 0.072 | 0.075398 | 0.055262
[7 empty] | 20 | 0.0003 | 0.072 | 0.037699 | 0.11052
[7 empty] | 11 | 0.0003 | 0.072 | 0.020735 | 0.20095
[7 empty] | 1440 | 0.0003 | 0.072 | 2.7143 | 0.0015351
| 390 | 0.072 | 0.015 | 2.3742 |  | Ripple
1/(2*f*R*C)
| % HARMONICS | [5 empty] | f | L | C | 2*PI*f*L | 1/(2*PI*f*C)
| 0.97965 | [5 empty] | 720 | 0.0003 | 0.072 | 1.3572 | 0.0030701
[7 empty] | 360 | 0.0004 | 0.072 | 0.90478 | 0.0061402
[7 empty] | 180 | 0.0005 | 0.072 | 0.56549 | 0.01228
[7 empty] | 60 | 0.0006 | 0.072 | 0.22619 | 0.036841
[7 empty] | 40 | 0.0007 | 0.072 | 0.17593 | 0.055262
[7 empty] | 20 | 0.0008 | 0.072 | 0.10053 | 0.11052
[7 empty] | 11 | 0.0009 | 0.072 | 0.062204 | 0.20095
[7 empty] | 1440 | 0.001 | 0.072 | 9.0478 | 0.0015351
2007-05-14
RWM 1 - 3.29 m-ohms
RWM 4 - 2.89 m-ohms
RWM 1 AND 4 total - 6.18 m-ohms
RWM 2 - 2.89 m-ohms
RWM 5 - 2.89 m-ohms
RWM 2 AND 5 total - 5.75 m-ohms
RWM 3 - 2.80 m-ohms
RWM 6 - 3.50 m-ohms
RWM 3 and 6 total - 6.30 m-ohms
From: Edmond D. McBride
Sent: Thursday, December 16, 2004 4:03 PM
To: Subrahmanya Ramakrishnan; Ronald E. Hatcher
Cc: Alfred von Halle; Charles L. Neumeyer; Richard J. Van Kirk; Michael
G. Bell
Subject: Resistance and Inductance Readings RWM Cables
Gentlemen,
The resistance and inductance readings of the RWM 4 conductor 500 MCM cables are completed. Cables were terminated in the test cell enclosure (B-RWM-01) and on all RWM coil terminals at the machine. To facilitate the test, the mid point of the RWM coils were lifted. (Refer to drawing B-4F1005, Sheet 1568).
Mid-points lifted are: B4F1568QN, TN, and UN.
Test equipment used:
Biddle DLRO Model 247000. Calibration due date: December 2, 2004.
Tektronix Type LC 130 Capacitance/Inductance Meter. Calibration due date: December 2005.
Data:
| Cable No |  | Resistance |  | Inductance
B4F1568P
| Red/Orange |  | 15.76 M-ohms | 49 micro-H
| Black/Blue |  | 15.75 M-ohms | 45 micro-H
B4F1568M
| Red/Orange |  | 15.79 M-ohms | 45 micro-H
| Black/Blue |  | 15.74 M-ohms | 48 micro-H
B4F1568M
| Red/Orange |  | 15.35 M-ohms | 40 micro-H
| Black/Blue |  | 15.37 M-ohms | 42 micro-H
| RWM | George Labik data
Resistance Measured Data
718 Inconel Bolts torqued to 35 ft lb
Resistance of Assembly 2 turns at the Current Feed Bars Interface
| Coil # | Bays | Resistance
milliohms
| 1 | AL | 0.57
| 2 | BC | 0.58
| 3 | DE | 0.58
| 4 | FG | 0.57
| 5 | HI | 0.55
| 6 | JK | 0.6
Resistance of Assembly 2 turns at the Test Cell JB
| 1 | AL
| 2 | BC | 2.86 *
| 3 | DE
| 4 | FG
| 5 | HI | 2.85 *
| 6 | JK
* Measured on 9 Nov 2004
RWM 1 - 3.29 m-ohms
RWM 4 - 2.89 m-ohms
RWM 1 AND 4 total - 6.18 m-ohms
RWM 2 - 2.89 m-ohms
RWM 5 - 2.89 m-ohms
RWM 2 AND 5 total - 5.75 m-ohms
RWM 3 - 2.80 m-ohms
RWM 6 - 3.50 m-ohms
RWM 3 and 6 total - 6.30 m-ohms
Raki, FYI, in your final SUMMARY table on the attachment, you have mislabeled the inductance column. Chas.
Begin forwarded message:
From: "Subrahmanya Ramakrishnan" <raki@pppl.gov>
Date: February 4, 2005 12:58:16 PM EST
To: "Charles L. Neumeyer" <cneumeyer@pppl.gov>, <ssabbagh@pppl.gov>, "Masayuki Ono" <mono@pppl.gov>, "Jonathan E. Menard" <jmenard@pppl.gov>, "Ronald E. Hatcher" <rhatcher@pppl.gov>, "Jim Bialek" <jbialek@pppl.gov>
Subject: RWM coil parameters
Hi
Following are the RWM loop parameters in a nutshell. The inductance
measurements were taken with another calibrated meter manufactured by
Electro-Scientific Industries (PPPL#913028) and calibrated (June 2005).
These numbers may be used for simulation purposes.:
SUMMARY OF THE LOOP RESISTANCE & INDUCTANCE DATA
RWM Coil LOOP Milliohms Microhenries
Coil 1 & 4 14.50 55.00
Coil 2 & 5 14.10 53.20
Coil 3 & 6 14.80 56.60
Attached table gives the details.
If you have any questions please let me know.
Thanks
Raki
Following was the earlier memo:
Hi
Regarding the parameters of the RWM circuit please note that the
complete installation of the power loop and termination of the cables
was completed only last week. Hence measurements of actual loop
resistances were made only after this work was complete. Earlier
measurements in December did not include parallel cabling and
terminations with actual lengths.
Please note the following:
A. Measurements of the power loop resistances are as follows:
1. Actual measurements of the coil were furnished by George Labik as
follows (all in milliohms):
Coil 1 AL 0.57
Coil 2 BC 0.58
Coil 3 DE 0.58
Coil 4 FG 0.57
Coil 5 HI 0.55
Coil 6 JK 0.6
2. Measurements of the loop resistances within the NSTX Test Cell were
made and are as follows (all in milliohms). Please note that this loop
is from the junction box inside the test cell to the coils connected in
series (anti-series).
2007-05-14
|  | Coils 1& 4 with cables inside the test cell: 6.1 milliohms | [5 empty] | 6.18
|  | Coils 2& 5 with cables inside the test cell: 5.8 milliohms | [5 empty] | 5.75
|  | Coils 3& 6 with cables inside the test cell: 6.4 milliohms | [5 empty] | 6.3
3. Measurements of the loop resistances from the RWM SDS were made and
are as follows (all in milliohms). Please note that this loop is from
the RWM SDS terminals to the Coils (coils included).
Coils 1& 4 with cables up to the RWM SDS in FCPC : 13.5 milliohms
Coils 2& 5 with cables up to the RWM SDS in FCPC : 13.5 milliohms
Coils 3& 6 with cables up to the RWM SDS in FCPC : 13.7 milliohms
4. The loop resistances from the RWM SPA to coil (Based on the lengths
of cables from the RWM SDS to the SPA terminals)were made and are as
follows (all in milliohms). Please note that this loop is from the RWM
SPA terminals to the Coils (coils included).
Coils 1& 4 with cables up to the RWM SPA - SU2 in FCPC : 14.5 milliohms
Coils 2& 5 with cables up to the RWM SDS - SU3 in FCPC : 14.1 milliohms
Coils 3& 6 with cables up to the RWM SDS - SU1 in FCPC : 14.8 milliohms
B. Regarding the inductances, all of us have the calculated values.
Measurement of the inductances up to the RWM SDS was made by Don
McBride. How ever the values are not reliable due to apparently
instrumentation problems.
Anyway the values obtained are (micro-henries-including coils):
Coils 1& 4 with cables up to the RWM SDS in FCPC : 80 microhenries
Coils 2& 5 with cables up to the RWM SDS in FCPC : 65 microhenries
Coils 3& 6 with cables up to the RWM SDS in FCPC : 110 microhenries
I am not sure as to why the inductances are so very different.
Raki
02/04/05 data
Following data are on the coils |  |  |  | Following data are on the coil group
RWM Coil | Bays | Milliohms |  | RWM Coil | Milliohms | Milliohms of coils only | Milliohms of cables in NTC only | Length of cables in NTC only | Length of cable loop in NTC only
Coil 1 | AL | 0.57 |  | Coil 1 & 4 | 6.1 | 1.14 | 4.96 | 227.5229 | 113.7615
Coil 2 | BC | 0.58 |  | Coil 2 & 5 | 5.8 | 1.13 | 4.67 | 214.2202 | 107.1101
Coil 3 | DE | 0.58 |  | Coil 3 & 6 | 6.4 | 1.18 | 5.22 | 239.4495 | 119.7248
Coil 4 | FG | 0.57
Coil 5 | HI | 0.55
Coil 6 | JK | 0.6
Calculated inductance of coil pair (two in series) is 32uHenries |  |  |  |  | Electro Scientific Industries |  | Impedance Meter 252 |  | Biddle used to take
[5 empty] | was used to take inductance measurements |  |  |  | Resistance measurements
Physical properties - 500 mcm cable |  |  | 61 strands
1 sq" = 1.273EE6 circ mils |  |  |  |  | 1 sq" = 645.2 sq.mm
Condtr. Diameter inches | Insulation Dia (Inch) |  | Semicon Dia (Inch) | Jacket Dia ((Inch) | Wt/ft | Min.Bend Radius (Inch) | Max Pulling tension Condtr (#) | Jacket Thickness (mils) | Conductor Area (sq.mm) | Conductor Area (sq.In)
0.813 |  |  |  | 1.4 |  |  |  |  | 253 | 0.39213
Resistance of 500 mcm cable = |  | 21.8 | milliohms per 1000 feet at 20*C
Calculated values of loop parameters. |  |  | Reference: Theraja Page 1071
Inductance of a loop of straight conductors |  |  |  | (u/2PI)*ln(D/r) + u1/8PI henries per meter
4*10^(-7)*2.3*(log(D/r))+(1/4)
Condtr.dia | Condtr.Radius | Insulation thickness | Length loop | Length loop | Distance bet. Condtrs.(D) | Distance bet. Condtrs.(D) | L | L | L | Loop Resistance (Cables & coils)
| cm | Inches | feet | cm | Inches | cm. | uH/meter | uH/feet of loop | uH | milliohms
RWM Coil Inductance & resistance- two coils 1 & 4 in series
4/C-500 mcm 600V cable from FCPC to NTC
0.813 | 1.0325 | 0.065 | 337 | 10271.76 | 0.943 | 2.3952 | 0.43622 | 0.13322 | 44.8952 | 14.6932
|  |  |  | For 2 conductors in parallel in each pole- assume 1/4th inductance |  |  |  |  | 11.2238 | 7.3466
500 mcm 600V cable within NTC - for a pair of coils 1 &4
0.813 | 1.0325 | 0.065 | 113.7615 | 3467.4495 | 0.943 | 2.3952 | 0.43622 | 0.13322 | 15.1553 | 4.96
500 mcm 600V cable within Room 233 between SDS & SPA - for a pair of coils
0.813 | 1.0325 | 0.065 | 24 | 731.52 | 0.943 | 2.3952 | 0.43622 | 0.13322 | 3.1973 | 1.0464
RWM Coil inductance/resistance - two coils 1 & 4 in series | [8 empty] | 32 | 1.14
TOTAL CALCULATED FOR THE LOOP OF COILS 1&4 | [8 empty] | 61.5764 | 14.493
TOTAL MEASURED FOR THE LOOP OF COILS 1&4 | [8 empty] | 55 | 14.5
RWM Coil Inductance & resistance- two coils 2 & 5 in series | [8 empty] | Induct. | Resis
4/C 500 mcm 600V cable from FCPC to NTC | [8 empty] | uH | mOhms
0.813 | 1.0325 | 0.065 | 340 | 10363.2 | 0.943 | 2.3952 | 0.43622 | 0.13322 | 45.2948 | 14.824
|  |  |  | For 2 conductors in parallel in each pole- assume 1/4th inductance |  |  |  |  | 11.3237 | 7.412
500 mcm 600V cable within NTC - for a pair of coils 1 &4
0.813 | 1.0325 | 0.065 | 107.1101 | 3264.7156 | 0.943 | 2.3952 | 0.43622 | 0.13322 | 14.2692 | 4.67
500 mcm 600V cable within Room 233 between SDS & SPA - for a pair of coils
0.813 | 1.0325 | 0.065 | 18 | 548.64 | 0.943 | 2.3952 | 0.43622 | 0.13322 | 2.398 | 0.7848
RWM Coil inductance/resistance - two coils 2 & 5 in series | [8 empty] | 32 | 1.13
TOTAL CALCULATED FOR THE LOOP OF COILS 2 & 5 | [8 empty] | 59.9909 | 13.9968
TOTAL MEASURED FOR THE LOOP OF COILS 2 & 5 | [8 empty] | 53.2 | 14.1
RWM Coil Inductance & resistance- two coils 3 & 6 in series | [8 empty] | Induct. | Resis
4/C 500 mcm 600V cable from FCPC to NTC | [8 empty] | uH | mOhms
0.813 | 1.0325 | 0.065 | 330 | 10058.4 | 0.943 | 2.3952 | 0.43622 | 0.13322 | 43.9626 | 14.388
|  |  |  | For 2 conductors in parallel in each pole- assume 1/4th inductance |  |  |  |  | 10.9907 | 7.194
500 mcm 600V cable within NTC - for a pair of coils 3 & 6
0.813 | 1.0325 | 0.065 | 119.7248 | 3649.211 | 0.943 | 2.3952 | 0.43622 | 0.13322 | 15.9497 | 5.22
500 mcm 600V cable within Room 233 between SDS & SPA - for a pair of coils
0.813 | 1.0325 | 0.065 | 30 | 914.4 | 0.943 | 2.3952 | 0.43622 | 0.13322 | 3.9966 | 1.308
RWM Coil inductance/resistance - two coils 3 & 6 in series | [8 empty] | 32 | 1.18
TOTAL CALCULATED FOR THE LOOP OF COILS 3 & 6 | [8 empty] | 62.937 | 14.902
TOTAL MEASURED FOR THE LOOP OF COILS 3 & 6 | [8 empty] | 56.6 | 14.8
SUMMARY OF THE LOOP INDUCTANCE & RESISTANCE DATA
RWM Coil LOOP | Milliohms | Milliohms of coils only
Coil 1 & 4 | 14.5 | 55
Coil 2 & 5 | 14.1 | 53.2
Coil 3 & 6 | 14.8 | 56.6