## Slide 1: MGI ACC Review
May 5th 2016

## Slide 2: Functional Overview
MGI uses current pulse from discharging a capacitor to quickly open a valve
Three separate systems
Each system consists of three main sections
Systems mounted in two equipment racks

## Slide 3: MGI (Power) System Overview

## Slide 4: Components
Charger Enclosure
  Capacitor Charger
  AC Power isolation
Capacitor Enclosure
  Capacitor: 550uF, 1000V -> 275J
  NC Discharge Relay
  NO Charge Relay
  Voltage & current sensors

## Slide 5: Components (cont.)
Control
  NI Compact-RIO system (real-time controller)
  Compact-RIO operated from remote GUI
  Charges & discharges capacitor during NSTX-U shot following configurable time sequence
  Monitors status of charger and capacitor
  Records measurements
  Observes all Hardware Interlock signals & reacts accordingly

## Slide 6: Safety Signals
Hardware Interlock Signals
  NO ESTOP, LOOP SET
  TVPS n
Equipment Rack Door Switches
Controller Related
  EPICS signals: system powered down and cap. Discharged between shots
  Controller Watchdog: forcing system into safe state if controller becomes unresponsive

## Slide 7: Hardware Interlock Signal ‘NO ESTOP’
Monitored in all MGI components
Inactive NO ESTOP:
  Removes AC power from charger
  Forces closure of discharge relay and capacitor discharge
  Removes power from trigger circuit

## Slide 8: Hardware Interlock Signal ‘LOOP SET’
Monitored in all MGI components
Inactive LOOP SET:
  Removes AC power from charger
  Forces closure of discharge relay and capacitor discharge
  Removes power from trigger circuit

## Slide 9: Hardware Interlock Signal ‘TVPS n’
One signal for each MGI system
Inactive TVPS:
  Removes AC power from charger
  Forces closure of discharge relay and capacitor discharge
  Prevents triggering of SCR

## Slide 10: Equipment Rack Door Switches
Two door switches in each rack
Ensure that rack doors are closed during operation
Inactive Door Switches:
  Prevent charging of capacitor
  Remove power from trigger circuit

## Slide 11: Control Software Safety
MGI only functions if under operator control
Controller monitors all HW interlock signals and reacts accordingly
Controller has built-in HW watchdog to force system into safe state if controller software becomes unresponsive

## Slide 12: Remote Control GUI

## Slide 13: Procedures
Capacitor Safing Procedure
  Process to ensure capacitor is discharged & grounded before any maintenance
MGI PTP
  Defines functional tests for a MGI system before installation
MGI ISTP
  Defines functional tests after installation, before operation
MGI Operation Procedure

## Slide 14: Additional Slides …

## Slide 15: Grounding Diagram