## Slide 1: Massive Gas Injector Power supply and control system CDR
10/16/2015

## Slide 2: Outline
Massive Gas Injector (MGI) Overview
Supply schematic
  Relays and interlocks
  Control signals
  High voltage considerations
Control system – NI cRIO chassis and modules
  Power
  Modules: DO, DI, AO, AI
  Sequence and state diagrams
System tests
Other necessities
  NEPA, Vacuum PLC, PCS, etc.
Timeline

## Slide 3: MGI Overview
Unmitigated disruptions in a tokamak discharge
  Cause excessive diverter heat loads
  Large halo currents
Injecting massive amounts of gas prior to the disruption can thermally quench the plasma and reduce the impact of disruptions
  NSTX-U is studying the effects of MGI at various poloidal locations around the plasma
  The injectors are installed; Power supplies and control systems are presented here

## Slide 5: Supply Schematic I
High Voltage Ross Relays control the connections to the dump resistor (RR1) and Glassman charging supply (RR2, RR3)
Solid State Relays
  SSR1 controls operation of RR1; SSR2 controls RR2 and RR3
  SSR3 controls power to Glassman supply
  SSR4 and SSR5 allows TVPS (24 VDC) to inhibit power to the charging supply, RR1, RR2, and RR3
  SSR6 and SSR7 allows NO-E-STOP (120 VAC) to inhibit power to the charging supply, RR1, RR2, and RR3
  Kirk key interlock is in series with NO-E-STOP
    Kirk keys lock the boxes shut. The supply is inside these boxes
Normal operation
  SSR1, SSR2, and SSR3 are controlled by NI cRIO Control System
  SSR4, SSR5, SSR6, and SSR7 are controlled by NO-E-STOP, TVPS and Kirk Key
  Loop Set/H.I.S. is monitored by NI cRIO Control System (discussed later)

## Slide 6: Supply Schematic II
Control signals
  Everything is coming from the NI cRIO system
  Digital: DR_OPEN, CHARGE_ENABLE, PC_ON, HV_ENABLE
  Analog: VC1
Several signals are continuously monitored, typically through voltage dividers
  VD_E_STOP, VD_TVPS, LOOP_SET (discussed later) to monitor permissives
  VD1, VD2 to monitor supply and capacitor voltage
  CM1 to monitor current out to MGI solenoid
High Voltage
  Suggested: Capacitor (-) is connected to chassis ground at all times
  As built: Capacitor (-) is connected to 250 Ohm which is connected to ground through the Glassman power supply
  The device that triggers the SCR is battery-powered, electrically isolated (via fiber optic) from the rest of the system and isolated by a transformer from the SCR
  System has been tested for functionality and high-potted to 2.5 kV

## Slide 7: Supply Schematic III
Cost Estimate
  I don’t have costs for all ‘big ticket’ items
    Glassman power supply, Ross Relays, Enclosure
  Around $500-$600 total for rest
Prototype is under construction at U-Wash
  Photographs are on the next slides

## Slide 21: NI cRIO Control System I
Chassis: CompactRIO-9065
  4-Slot Artix-7 FPGA
  667 MHz dual-core ARM Cortex-A0
  1GB NV Storage, 512 MG DDR3 Memory
  NI Linux Real-Time OS
  Ethernet
Modules
  NI 9201: 8-ch Analog Input, ±10V, 12-Bit 500 kS/s
  NI 9263: 4-ch Analog Output, ±10V, 16-Bit, 100 kS/s/ch
  NI 9401: 8-Ch, 100 ns, 5V/TTL Digital I/O Module
  NI 9472: 8-Ch, 100 us, 6-30 V Sourcing DO Module
Power
  Chassis and DO Module require external power supply
    10V, 2A ‘brick’ style supply, plugged into a power strip located in rack would suffice
NI Quote: $4419

## Slide 23: NI cRIO Control System II
State Diagram
  See attachment
Software issues
  Using existing NI software license (Labview, FPGA and Realtime): FREE, but with risks
    I have never had ‘official’ NI LV training; Software may not be optimal
    Paul S and I would be ‘sharing’ the license
  Upgrading to the newest ‘embedded’ suite software: $5700
    Still time sharing the license, no training
  New embedded suite with online training: $9900
    Two complete software setups
    Access to online training – go at my own pace
    Software would more likely be optimal
  Just training (1-year, unlimited classroom and virtual, not online): $6210
    Still time sharing license, no online training, may have to travel to classroom
  Just the bare minimum courses, classroom training (off-campus)
    Core 1 and Core 2 - $4000
    Embedded Control and Monitoring - $3210

## Slide 24: System Tests
Power inhibit tests
  No_E_stop, TVPS_Permissive, Kirk Key
High-pot/isolation tests
Software E stop
Power on/No SCR trigger
Vcap > 1.05 x Vrequest
Basic Timing/Functional
This list needs to be formalized

## Slide 25: Other necessities
NEPA form - done
Vacuum PLC – Will need TVPS permissive to racks
PCS – Will need trigger signal to racks
NO-E-STOP, Loop set / H.I.S. signals to racks
Kirk Keys
Others?

## Slide 26: Timeline
MGI Power supply: Mid-December
Control system: Early December
Install Electrical system HW: Mid-December
Test supply into dummy load: Early January
Test supply into MGI valve: Early January