## Template
Item | Originator | Concern/Recommendation | Committee Comment/Action | Current Status | Verification Information
1 | Sichta | For during-shot digitized signals, the A/D trigger time and the data sampling time must be correlated. Or, also digitize a 3rd "timing mark" channel. | Concur: a dedicated timing channel is preferred. Action Schmitt
2 | Lawson | Define EPICS interface: Stored settings, Waveforms, Shot #, etc. | Concur: Action Schmitt
3 | Lawson | Battery status needs moitoring. Replace with power supply | Should be considered. Concern could be addressed administratively if battery is used in its proposed configuration. Action: Raman/Schmitt
4 | Gerhardt | At end of charging, ensure that disabling high voltage does not short the Glassman Supply output. | Concur: Action Schmitt
5 | Gerhardt | The Ip Calculator has an "ITF < allowable" signal. Assess of this should be incororated into the MGI Controls | Concur: Concur: Action Schmit, Lawson, Gerhardt, Mozulay
6 | Gerhardt | On the "NI Chassis V20151014a"inputs; Check the interface for "Loop Set/HIS". Contact closure or 120VAC? | Concur: Schnitt/Camp
7 | Lawson | 24 V supply to control logic rather than 10V (as shown) | The more standard 24 Volt supply is preferable. Action: Schmitt/Raman to consider
8 | Gerhardt | Do not co-mingle the High Voltage and A/C Control power in Box #2 | Power and control cabling must be seperated. Action Schmitt/Raman
9 | Sichta | On the Power Supply drawing, show I/O Voltages. Also correct the drawing to remove the wire in parallel with R8 (110 ohm) | Concur: Action Schmitt
10 | Gerhardt | Make a "grounding" diagram for the next review. Should show ground classes and locations of electrical breaks | Concur: Action Schmitt
11 | Gerhardt | Confirm that the gas delivery system P&ID's have been updated to show the MGI configuration. | Concur: Action Schmitt/Blanchard
12 | Gerhardt | Develop the plan/requirements for electrical insulation tests (Hi-Pots) when the system is installed. This will help determinewhere to ensure that sufficient insulation exists. | Concur: Action Schmitt
13 | vonHalle | Work packages for system interfaces in the NTC should be prepared/released as soon as possible | Concur: Action Schmitt
14 | Lawson | The MGI capacitor discharge system meets the criteria of a Cap Bank as described in the PPPL Health and Safety Manual. Needs to meet specific safety requirements. (Access procedure, etc.) | Concur: Action Schmitt/Camp/Anderson. See Chit #15
15 | Westover | Recommend development of an access procedure outlining a safe and practical process for safing all parts of the system. Needs to include interlocks, required PPE, visibility of conditions, discharge and grounding sticks, rtc. | Concur. Combined action with Chit #14. Action Schmitt/Westover.