Design Review documentation – Results

Title:	MGI Electrical		WP#: 	2113	 (ENG-032)

Type of Review:	 Peer	 CDR	 PDR	  FDR

Cog Individual:	J. Schmitt		Date of Review: 	2/18/16

Review Attendees:

Chair: T. N. Stevenson		R. Raman (remote)		J. E. Lawson

F. Hoffman		S. Gerhardt		Raki Ramakrishnan

N. Rahman		M. Ono		S. Aslam, PMO

R. Kaita		D. Westover		A. von Halle (RLM)

P. Sichta		F. Jones		H. Schneider

R. Ellis

Items Reviewed:	Sat.	Unsat.	Comments or n/a if not applicable

Appropriate requirements identified 			Supporting MGI Mechanical WP 2165

Development plans and schedules			MGI Schedule (Gerhardt)

Regulatory compliance including USQD and NEPA			NEPA 1592

Disposition of CHITS from previous reviews			CDR, PDR, Software

Cost objectives			WAF

Other review objectives addressed			n/a

SUMMARY OF RESULTS:

Plans for MGI use and electrical requirements were covered. Chits from previous reviews were discussed. Drawings for circuit power supply, control, and grounding were presented. An IP is in progress. An Access procedure was discussed including the cap bank grounding and bleed resistors. Several key Interlocks were evaluated including E stop. Grounding diagrams. Cabling requirements and data sheet. Pressure transducer considered for next year. NI Controls. CWDs. Testing procedure. ISTP. Timeline.

Disposition: [check one]

Acceptable

X	 Acceptable pending resolution of concerns- CHITS identified above must be resolved prior to installation.

_______ Incomplete - Additional design work is required prior to another design review.

_______ Unsuccessful – Corrective actions must be taken and another review process must be initiated.

RLM Concurrence:                  TNS for AvH___________________Date: _3/1/16___

DR Chairperson Signature: ___T. N. Stevenson___________________   Date: __3/1/16__

Distribution:   Review Board Members, Operations Center, Cognizant Design Engineer, System Engineer(s), Head, Office of Project Management, Attendees, QA, ES&H, Security, Requesting & Performing Dept. Heads, and Associate Director for Engineering and Infrastructure